## 2MW机型总点表
序号 | 目录 |  | 名称 | Config |  |  | 单位 | 描述 | 变量名
|  |  |  | 倍数 | 数据类型 | 地址
1 | Turbine to PPM | 有功 | 有功握手信号 | 1 | I16 | 4000 | - |  | V_SentToPPMAPCount
2 |  |  | 有功状态 | 1 | I16 | 4001 | - |  | V_APStateToPPM
3 |  |  | 有功3秒均值 | 1 | I32 | 4002-4003 | W |  | V_GridRealPower3Sec
4 |  |  | 当前可利用功率 | 1 | I32 | 4004-4005 | W |  | V_AvailablePowerToPPM
5 |  |  | 额定功率 | 1 | I32 | 4006-4007 | W |  | P_RatedPower
6 |  |  | 当前有功限值 | 1 | I32 | 4008-4009 | W |  | V_PM_ActivePowerSetpointW
7 |  |  | 累计有功发电量 | 1 | I32 | 4010-4011 | kWh |  | S_TotalProduction
8 |  |  | 累计发电时间 | 1 | I32 | 4012-4013 | s |  | S_TotalOperation
9 |  |  | 当前风速3秒均值 | 1 | I16 | 4014 | 0.1m/s |  | V_WindSpeed3Sec
|  |  | PPM有功通讯中断间隔限值 | 1 | I32 | 4015-4016 | S | 该值为设定PPM有功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5007故障 | P_APComChangeTime
|  |  | 预留 |  | I32 | 4017-4018
|  |  | 预留 |  | I32 | 4019-4020
13 |  | 无功 | 无功握手信号 | 1 | I16 | 4021 | - |  | V_SentToPPMRPCount
14 |  |  | 无功状态 | 1 | I16 | 4022 | - |  | V_RPStateToPPM
15 |  |  | 无功3秒均值 | 1 | I32 | 4023-4024 | kVar |  | V_GridReactivePower3Sec
|  |  | PPM无功通讯中断间隔限值 | 1 | I32 | 4025-4026 | S | 该值为设定PPM无功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5008故障 | P_RPComChangeTime
|  |  | 当前无功限值 | 1 | I32 | 4027-4028 | Var |  | V_PM_ReactivePowerSetpoint
1 | PPM to Turbine | 有功 | PPM有功握手信号 | 1 | I16 | 4029 | - |  | V_APCountFromPPM
2 |  |  | PPM有功控制模式 | 1 | I16 | 4030 | - |  | V_APStateFromPPM
3 |  |  | 有功设定值 | 1 | I32 | 4031-4032 | W |  | V_ActivePowerSetpoint
|  |  | 预留 |  | I32 | 4033-4034
5 |  | 无功 | PPM无功握手信号 | 1 | I16 | 4035 | - |  | V_RPCountFromPPM
6 |  |  | PPM无功控制模式 | 1 | I16 | 4036 | - |  | V_RPStateFromPPM
7 |  |  | 无功设定值 | 1 | I32 | 4037-4038 | Var |  | V_ReactivePowerSetpoint
|  |  | 预留 |  | I32 | 4039-4040
|  |  | 预留 |  | I32 | 4041-4042
1 | Safety Chain |  | 安全链状态 | 1 | I16 | 100 | 字符串 | 1:"EStop Error" 2:"SC1 Error" 3:"SC2 Error" 4:"Safety Ok" | V_SafetyChainStateText
2 |  |  | 安全链故障 | 1 | I16 | 101 | 字符串 | 1:"Detecting..." 2:"Emergency Stop Nacelle Ext." 3:"Emergency Stop Nacelle" 4:"Emergency Stop Tower Base" 5:"EStop Awaiting reset" 6:"SafetyChain MCB" 7:"Vibration" 8:"WP2035 (R) Overspeed" 9:"WP2035 (G) Overspeed" 10:"SC1 Awaiting reset" 11:"Manual Safety Stop Nacelle" 12:"WP4000 Controller relay" 13:"SC2 Awaiting reset" 14:"None" | V_SafetyChainErrorText
3 |  |  | 安全链复位模式 | 1 | I16 | 102 | 字符串 | 1:"OFF" 2:"MANUAL" 3:"AUTOMATIC" 4:"ON" 5:"UNKNOWN" | V_ResetModeText
4 |  |  | 上电复位模式 | 1 | I16 | 103 | 字符串 | 1:"Done" 2:"Executing" 3:"None" 4:"Pending" | V_ResetOnBootText
5 |  |  | 机舱急停按钮状态 | 1 | I16 | 104 | 0/1 | The current condition on input | DI_EmergencyStopNacelleExternal
6 |  |  | 机舱柜急停按钮状态 | 1 | I16 | 105 | 0/1 | The current condition on input | DI_EmergencyStopNacellePanel
7 |  |  | 塔基急停按钮状态 | 1 | I16 | 106 | 0/1 | The current condition on input | DI_EmergencyStopTowerBase
8 |  |  | 急停继电器状态 | 1 | I16 | 107 | 0/1 | The current condition on input | DI_EmergencyStopRelay
9 |  |  | 安全链总状态 | 1 | I16 | 108 | 0/1 | The current condition on input | DI_SafetyChainMCCB
10 |  |  | 振动开关状态 | 1 | I16 | 109 | 0/1 | The current condition on input | DI_VibrationSensor
11 |  |  | 安全链继电器1状态 | 1 | I16 | 110 | 0/1 | The current condition on input | DI_SafetyChainRelayOne
12 |  |  | WP2035主轴超速模块状态 | 1 | I16 | 111 | 0/1 | Shows the rotor wp2035 overspeed detection, the current condition on input | DI_FeedbackRotorOverspeed
13 |  |  | WP2035发电机超速模块状态 | 1 | I16 | 112 | 0/1 | Shows the generator wp2035 overspeed detection, the current condition on input | DI_FeedbackGeneratorOverspeed
14 |  |  | 机舱柜安全停机 | 1 | I16 | 113 | 0/1 | The current condition on input | DI_SafetyChainManualStopNacelle
15 |  |  | WP4100安全链输入信号 | 1 | I16 | 114 | 0/1 | The current condition on input | Chain_In_Signal
16 |  |  | WP4100安全链输出信号 | 1 | I16 | 115 | 0/1 | The current condition on input | Chain_Out_Signal
17 |  |  | 变桨安全链状态 | 1 | I16 | 116 | 0/1 | The current condition on input | DI_SafetyChainRelayTwo
18 |  |  | 安全链继电器2状态 | 1 | I16 | 117 | 0/1 | The current condition on input | DI_SafetyChainRelayTwo
19 |  |  | 塔基手动停机 | 1 | I16 | 118 | 0/1 | The current condition on input | DI_ManualStopTowerBase
20 |  |  | 机舱手动停机 | 1 | I16 | 119 | 0/1 | The current condition on input | DI_ManualStopNacelle
21 |  |  | 手动停止顺时针偏航 | 1 | I16 | 120 | 0/1 | The current condition on input | DI_YawEndStopCw
22 |  |  | 手动停止逆时针偏航 | 1 | I16 | 121 | 0/1 | The current condition on input | DI_YawEndStopCcw
23 |  |  | 本地复位安全链信号 | 1 | I16 | 122 | 0/1 | The current condition on input | DI_SafetyChainResetPulse
24 |  |  | 远程复位安全链信号 | 1 | I16 | 123 | 0/1 | The current condition on output | DO_ResetSafetyChain
25 | Operate |  | 机组运行状态 | 1 | I16 | 200 | 字符串 | 1:"Starting" 2:"Service" 3:"Yaw into wind" 4:"Selftest run check" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Freewheel init" 12:"Freewheel G1" 13:"Grid connect G1" 14:"Operation G1" 15:"LVRT" 16:"Freewheel G1G1" 17:"Battery test" 18:"Pitch Service Test" 19:"B200" 20:"B199" 21:"B99" 22:"B50" 23:"None" | V_ActualOperateStateTxt
26 |  |  | 运行状态剩余时间 | 1000 | I32 | 201-202 | s | Up/down counter estimating the time until the end of this state. When it is zero, the state changes. Shows the lowest of the timers, except in the starting state where the highest one is shown. | V_EventTimeOut
27 |  |  | 计时名称 | 1 | I16 | 203 | 字符串 | 1:"Secs until start" 2:"Force start" 3:"Start wind" 4:"Brake cool" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Gen.rpm OK" 12:"State timeout" 13:"Connect window" 14:"Phase Drop" 15:"Power Recovery" 16:"None" | V_ActualOperateTimerTxt
28 |  |  | 运行步骤 | 1 | I16 | 204 | 字符串 | 1:"None" 2:"Waiting for MDS" 3:"Waiting for Grid" 4:"STEP 1" 5:"STEP 2" 6:"STEP 3" 7:"STEP 4" 8:"STEP 5" | V_ActualOperateStepTxt
29 |  |  | 运行模式 | 1 | I16 | 205 | 字符串 | 1:"RUN-AUTO" 2:"RUN-SERVICE" 3:"SERVICE" 4:"UNKNOWN" | V_OperateModeText
30 |  |  | 变桨模式 | 1 | I16 | 206 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"ESTOP" 4:"UNKNOWN" | V_PitchModeText
31 |  |  | 变频器模式 | 1 | I16 | 207 | 字符串 | 1:"RUN" 2:"STOP" 3:"UNKNOWN" | V_InverterModeText
32 |  |  | 变桨MDS模式 | 1 | I16 | 208 | 字符串 | 1:"SAFETY" 2:"OPERATE" 3:"SERVICE" 4:"BATTERYTEST1" 5:"BATTERYTEST2" 6:"BATTERYTEST3" 7:"TEST" 8:"SIMULATE" 9:"UNKNOWN" | V_MDSModeText
33 |  |  | 变桨位置极限 | 100 | I32 | 209-210 | ° | Min. allowed pitch angle, sent to Pitch Controller | V_PitchPositionLimit
34 |  |  | 变桨速度极限 | 100 | I32 | 211-212 | °/s | Max. allowed pitch speed, sent to Pitch Controller | V_PitchSpeedLimit
35 |  |  | 发电机转速极限 | 100 | I32 | 213-214 | rpm | Max. allowed generator rpm, sent to Pitch Controller. | V_GeneratorRpmLimit
36 |  |  | 转矩极限 | 10 | I32 | 215-216 | Nm | Max. allowed torque, sent to Torque Controller. | V_TorqueLimit
37 |  |  | 制动冷却时间 | 1000 | I32 | 217-218 | S | Time until brakes have been cooled down after applying. When 0 the turbine can be started. This timer uses value from the parameter Brake Cool xxx s p. 169. The timer can be used as state timer in the operational state Starting (see 2.6.2.2). The timer counts down to 0 if mechanical brake is released (3.3#16 "HYDRAULIC VALVE BRAKER OPEN" p. 658 = 0) or if "Zero rpm" ( Rotor xxxxxxxx.xxx rpm p. 331 < 2 rpm and Generator xxxxxxxx.x rpm p. 306 < 2 rpm * Gear Ratio xxx.xx p. 351) is reached. | V_BrakeCoolTime
386 | Turbine Status |  | 风机限功状态 | 1 | I16 | 3200 | 0/1 |  | V_PowerReducedOperation
387 |  |  | 风机发电状态 | 1 | I16 | 3201 | 0/1 |  | V_ToPM_P_GridConnect
388 |  |  | 风机待机状态 | 1 | I16 | 3202 | 0/1 |  | V_WT_StandbyMode
389 |  |  | 风机停机状态 | 1 | I16 | 3203 | 0/1 |  | V_WT_Stopstatus
390 |  |  | 风机维护状态 | 1 | I16 | 3204 | 0/1 |  | V_WT_Servicestatus
391 |  |  | 机组有功功率设定值（可写） | 1000 | I32 | 3205-3206 | kw |  | B_ToPM_P_Sp_kW
392 |  |  | 机组无功功率设定值（可写） | 1000 | I32 | 3207-3208 | kVAr |  | B_ToPM_Q_Sp_kVAr
392+ |  |  | 机组控制(可写) | 1 | I16 | 3209 | - | 1：启动 2：停止 3：复位 | V_RemoteCommand
38 | Yaw |  | 当前偏航程序 | 1 | I16 | 300 | / | Shows the active yaw program (0,30,50,60, 70, 80, 100, 230 or 240). | V_ActiveControlProgram2
39 |  |  | 当前偏航状态 | 1 | I16 | 301 | 字符串 | 1:"STOPPED" 2:"START CW" 3:"STARTCCW" 4:"RUN. CW" 5:"STOPPING" 6:"RUN. CCW" 7:"STOPPING" | V_ActualYawStateTxt
40 |  |  | 偏航自动模式 | 1 | I16 | 302 | 0/1 |  | DI_YawAutomodeSwitch
41 |  |  | 顺时针解缆限位开关 | 1 | I16 | 303 | 0/1 | The current condition on input | DI_YawEndStopCw
42 |  |  | 逆时针解缆限位开关 | 1 | I16 | 304 | 0/1 | The current condition on input | DI_YawEndStopCcw
43 |  |  | 顺时针偏航 | 1 | I16 | 305 | 0/1 | The current condition on output | DO_YawMotorCw
44 |  |  | 顺时针偏航继电器反馈 | 1 | I16 | 306 | 0/1 | The current condition on input | DI_YawMotorCWContactor
45 |  |  | 逆时针偏航 | 1 | I16 | 307 | 0/1 | The current condition on output | DO_YawMotorCcw
46 |  |  | 逆时针偏航继电器反馈 | 1 | I16 | 308 | 0/1 | The current condition on input | DI_YawMotorCCWContactor
47 |  |  | 偏航系统供电回路反馈 | 1 | I16 | 309 | 0/1 | The current condition on input | DI_MCBYawSystemFB
48 |  |  | 偏航半压制动 | 1 | I16 | 310 | 0/1 | The current condition on output | DO_MechanicalYawReduceBrakeValve
49 |  |  | 偏航全压制动 | 1 | I16 | 311 | 0/1 | The current condition on output | DO_MechanicalYawFullBrakeValve
50 |  |  | 偏航电磁制动 | 1 | I16 | 312 | 0/1 | The electrical yaw brake | DO_YawBrakeelectrical
51 |  |  | 机舱相对正北角度 | 10 | I16 | 313 | ° | Shows the position of the nacelle in context to a circle were 0°is North. | V_NacelleDirection
52 |  |  | 机舱相对风向角度 | 10 | I16 | 314 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned correctly according to the wind direction. | V_RelaWindVaneDirection3Sec
53 |  |  | 偏航传感器A | 1 | I16 | 315 | 0/1 | The current condition on input | DI_YawCountSensorA
54 |  |  | 偏航传感器B | 1 | I16 | 316 | 0/1 | The current condition on input | DI_YawCountSensorB
55 |  |  | 解缆传感器（0=逆时针/1=顺时针） | 1 | I16 | 317 | 0/1 | Shows which way the cable is twisted (1 = Cw / 0 = Ccw). | DI_YawCableTwist
56 |  |  | 解缆角度 | 10 | I32 | 318-319 | ° | Shows how many degrees the cables in the tower are twisted. To reset the value | V_NacelleTwistDeg
57 |  |  | 偏航程序模式 | 1 | I16 | 320 | 0/1 | Shows the active yaw program. | V_YawParameterSet
58 |  |  | 顺时针偏航倒计时 | 1000 | I32 | 321-322 | s | Yaw delay for the CW direction. | V_StartYawCwDelay
59 |  |  | 逆时针偏航倒计时 | 1000 | I32 | 323-324 | s | Yaw delay for the CCW direction. | V_StartYawCcwDelay
67 | Pitch |  | 功率设定值 | 1000 | I32 | 502-503 | KW | Power setpoint from Operate to the PID controller | V_PitchPowerSetpoint
68 |  |  | 变桨角度 | 100 | I32 | 504-505 | ° | Simple average of the actual 3 pitch angles. | V_PitchAngle
69 |  |  | 变桨角度设定值 | 100 | I32 | 506-507 | ° | Angle Setpoint sent to the Blade controller | V_PitchCtrl_AngleSetPoint
70 |  |  | 变桨速度 | 100 | I32 | 508-509 | °/s | Pitch speed. | V_PitchAngleSpeed
71 |  |  | PID输入模式 | 1 | I16 | 510 | 字符串 | 1:"SPEED" 2:"AUTO" | V_PID_ModeTxt
72 |  |  |  | 1 | I16 | 511 | 字符串 | 1:"ENABLED" 2:"DISABLED" | V_RippleDamperEnableTxt
73 |  |  |  | 1 | I16 | 512 | 字符串 | 1:"ENABLED" 2:"DISABLED" | V_ZeroPointDamperEnableTxt
75 | Blade Controller |  | 变桨当前模式 | 1 | I16 | 600 | 字符串 | 1:"Safety" 2:"Operate" 3:"Service" 4:"Batterytest1" 5:"Batterytest2" 6:"Batterytest3" 7:"Test mode" 8:"Simulate Pitch" | V_MDSCurrentModeTxt
76 |  |  | 变桨速度限值 | 100 | I32 | 601-602 | ° | Pitch speed limit from the pitch regulator. | V_PitchSpeedLimit
77 |  |  | 变桨角度设定值 | 100 | I32 | 603-604 | ° |  | V_PitchAngleSetPoint
78 |  |  | 1号桨叶角度 | 100 | I32 | 605-606 | ° | Actual pitch angle blade 1. | V_MDSActPitchAngleA
79 |  |  | 2号桨叶角度 | 100 | I32 | 607-608 | ° | Actual pitch angle blade 2. | V_MDSActPitchAngleB
80 |  |  | 3号桨叶角度 | 100 | I32 | 609-610 | ° | Actual pitch angle blade 3. | V_MDSActPitchAngleC
81 |  |  | 1号桨叶当前故障 | 1 | I16 | 611 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults1
82 |  |  | 2号桨叶当前故障 | 1 | I16 | 612 | / | Lists active faults on Blade 2. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults2
83 |  |  | 3号桨叶当前故障 | 1 | I16 | 613 | / | Lists active faults on Blade 3. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults3
84 |  |  | 1号桨叶当前报警 | 1 | I16 | 614 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings1
85 |  |  | 2号桨叶当前报警 | 1 | I16 | 615 | / | Lists active warnings on Blade 2. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings2
86 |  |  | 3号桨叶当前报警 | 1 | I16 | 616 | / | Lists active warnings on Blade 3. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings3
87 |  |  | Modbus驱动器控制 | 1 | I16 | 617 | 字符串 | 1:"Run" 2:"Config" | V_ModbusMasterControlTxt
88 |  |  | 1号桨叶MDS通讯OK | 1 | I16 | 618 | 0/1 | Indicates communication status towards Blade 1. | V_Unit1NodeDead
89 |  |  | 2号桨叶MDS通讯OK | 1 | I16 | 619 | 0/1 | Indicates communication status towards Blade 2. | V_Unit2NodeDead
90 |  |  | 3号桨叶MDS通讯OK | 1 | I16 | 620 | 0/1 | Indicates communication status towards Blade 3. | V_Unit3NodeDead
91 |  |  | 复位变桨通讯状态（可写） | 1 | I16 | 621 | 0/1 | This setting must be updated to 1 to reset MDS communication related statistics. After the update the setting will automatically return to 0. | V_MDSResetCommStats
92 |  |  | 通讯信息 | 1 | I16 | 622 | / |  | V_MDS_BrcMsgsTx
93 |  |  | MDS1读取的请求数量 | 1 | I16 | 623 | / | Number of read requests sent. | V_ReadReqTx_Unit1
94 |  |  | MDS1收到的响应数量 | 1 | I16 | 624 | / | Number of received reponses. | V_ResponseRx_Unit1
95 |  |  | MDS1丢失的响应数量 | 1 | I16 | 625 | / | Number of missing responses. | V_MissingResponse_Unit1
96 |  |  | CRC故障 | 1 | I16 | 626 | / |  | V_CrcErrors_Unit1
97 |  |  | MDS1结构故障数量 | 1 | I16 | 627 | / | Number of responses received containing framing errors. | V_FrameErrors_Unit1
98 |  |  | MDS2读取的请求数量 | 1 | I16 | 628 | / | Number of read requests sent. | V_ReadReqTx_Unit1
99 |  |  | MDS2收到的响应数量 | 1 | I16 | 629 | / | Number of received reponses. | V_ResponseRx_Unit2
100 |  |  | MDS2丢失的响应数量 | 1 | I16 | 630 | / | Number of missing responses. | V_MissingResponse_Unit2
101 |  |  | CRC故障 | 1 | I16 | 631 | / |  | V_CrcErrors_Unit2
102 |  |  | MDS2结构故障数量 | 1 | I16 | 632 | / | Number of responses received containing framing errors. | V_FrameErrors_Unit2
103 |  |  | MDS3读取的请求数量 | 1 | I16 | 633 | / | Number of read requests sent. | V_ReadReqTx_Unit1
104 |  |  | MDS3收到的响应数量 | 1 | I16 | 634 | / | Number of received reponses. | V_ResponseRx_Unit3
105 |  |  | MDS3丢失的响应数量 | 1 | I16 | 635 | / | Number of missing responses. | V_MissingResponse_Unit3
106 |  |  | CRC故障 | 1 | I16 | 636 | / |  | V_CrcErrors_Unit3
107 |  |  | MDS3结构故障数量 | 1 | I16 | 637 | / | Number of responses received containing framing errors. | V_FrameErrors_Unit3
108 |  |  | 变桨1软件版本 | 1 | I32 | 638-639 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | V_MDSSWVersionA
109 |  |  | 变桨1当前模式 | 1 | I16 | 640 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man." | V_MDSUnitACurrentModeTxt
110 |  |  | 变桨1以安全速度切出 | 1 | I16 | 641 | 字符串 | 1:"Normal" 2:"Safety" | V_MDS1SafetySpeedOut
111 |  |  | 变桨1当前故障 | 1 | I16 | 642 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults1
112 |  |  | 变桨1当前报警 | 1 | I16 | 643 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings1
113 |  |  | 变桨1电机状态 | 1 | I16 | 644 | 字符串 | 1:"Stopped" "Started" | V_MDS1MotorControl
114 |  |  | 变桨1制动状态 | 1 | I16 | 645 | 字符串 | 1:"Released" 2:"Activated" | V_MDS1BrakeControl
115 |  |  | 变桨1电池状态 | 1 | I16 | 646 | 字符串 | 1:"Disconnected" 2:"Connected" | V_MDS1BatteryControl
116 |  |  | 变桨1进程状态 | 1 | I16 | 647 | 字符串 | 1:"Disable" 2:"Enable" | V_MDS1Process
117 |  |  | 变桨1轮毂维护使能 | 1 | I16 | 648 | 0/1 | Specifies the hub service state on the MDS unit. | V_MDSHubServiceAEnabled
118 |  |  | 变桨2软件版本 | 1 | I32 | 649-650 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | V_MDSSWVersionB
119 |  |  | 变桨2当前模式 | 1 | I16 | 651 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man." | V_MDSUnitBCurrentModeTxt
120 |  |  | 变桨2以安全速度切出 | 1 | I16 | 652 | 字符串 | 1:"Normal" 2:"Safety" | V_MDS2SafetySpeedOut
121 |  |  | 变桨2当前故障 | 1 | I16 | 653 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults2
122 |  |  | 变桨2当前报警 | 1 | I16 | 654 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings2
123 |  |  | 变桨2电机状态 | 1 | I16 | 655 | 字符串 | 1:"Stopped" "Started" | V_MDS2MotorControl
124 |  |  | 变桨2制动状态 | 1 | I16 | 656 | 字符串 | 1:"Released" 2:"Activated" | V_MDS2BrakeControl
125 |  |  | 变桨2电池状态 | 1 | I16 | 657 | 字符串 | 1:"Disconnected" 2:"Connected" | V_MDS2BatteryControl
126 |  |  | 变桨2进程状态 | 1 | I16 | 658 | 字符串 | 1:"Disable" 2:"Enable" | V_MDS2Process
127 |  |  | 变桨2轮毂维护使能 | 1 | I16 | 659 | 0/1 | Specifies the hub service state on the MDS unit. | V_MDSHubServiceBEnabled
128 |  |  | 变桨3软件版本 | 1 | I32 | 660-661 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | V_MDSSWVersionC
129 |  |  | 变桨3当前模式 | 1 | I16 | 662 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man." | V_MDSUnitCCurrentModeTxt
130 |  |  | 变桨3以安全速度切出 | 1 | I16 | 663 | 字符串 | 1:"Normal" 2:"Safety" | V_MDS3SafetySpeedOut
131 |  |  | 变桨3当前故障 | 1 | I16 | 664 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults3
132 |  |  | 变桨3当前报警 | 1 | I16 | 665 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings3
133 |  |  | 变桨3电机状态 | 1 | I16 | 666 | 字符串 | 1:"Stopped" "Started" | V_MDS3MotorControl
134 |  |  | 变桨3制动状态 | 1 | I16 | 667 | 字符串 | 1:"Released" 2:"Activated" | V_MDS3BrakeControl
135 |  |  | 变桨3电池状态 | 1 | I16 | 668 | 字符串 | 1:"Disconnected" 2:"Connected" | V_MDS3BatteryControl
136 |  |  | 变桨3进程状态 | 1 | I16 | 669 | 字符串 | 1:"Disable" 2:"Enable" | V_MDS3Process
137 |  |  | 变桨3轮毂维护使能 | 1 | I16 | 670 | 0/1 | Specifies the hub service state on the MDS unit. | V_MDSHubServiceCEnabled
138 |  |  | 上一次电池测试2/3时间 | 1 | I64 | 671-674 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | B_MDSLastBatteryTest2Time
139 |  |  | 1号桨叶上一次电池测试电压 | 1 | I16 | 675 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 1. | B_MDSBatteryVoltageA
140 |  |  | 2号桨叶上一次电池测试电压 | 1 | I16 | 676 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 2. | B_MDSBatteryVoltageB
141 |  |  | 3号桨叶上一次电池测试电压 | 1 | I16 | 677 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 3. | B_MDSBatteryVoltageC
142 |  |  | 电池测试请求信号 | 1 | I16 | 678 | 0/1 | The MDS system has requested the operation program to perform a battery test 2 or 3. | V_MDSRequestBatteryTest
|  |  | 手动电池测试请求（可写） |  | I16 | 679 | 0/1 |  | V_MDSManualRequestBatteryTest
143 |  |  | 电池测试故障 | 1 | I16 | 680 | 0/1 | Indicates if the latest battery test failed. A successfull battery test is required before the turbine is allowed to start. | B_MDSBatteryTestFailed
144 | Torque |  | 转矩控制器状态 | 1 | I16 | 700 | 字符串 | 1:"OFF (Limited to 0Nm)" 2:"L PI Grid Connect X.Ys" 3:"L PI Ramp Lower Limit" 4:"L PI Ramp to G1G1" 5:"L PI Active" 6:"Speed Ctrl. Await Torque" 7:"Critical Torque" 8:"Critical Torque" 9:"Power-Speed Red. ZkW" 10:"Power Red. ZkW" 11:"Power Control Rated Power" 12:"Speed Ctrl. Await Op. RPM SP" 13:"Exiting Power Control" 14:"Torque Table Lookup" | V_TorqueStateText
145 |  |  | 转矩设定值 | 10 | I32 | 701-702 | Nm | Torque Setpoint calculated by the torque controller | V_TorqueSPNm
146 |  |  | 转矩设定百分比 | 100 | I16 | 703 | % | Shows torque setpoint in percents | V_TorqueSetpointPct
147 |  |  | 发电机转速 | 100 | I32 | 704-705 | rpm |  | V_LocalControlRpm
148 |  |  | PI控制器的发电机转速设定值 | 100 | I32 | 706-707 | rpm | Generator speed setpoint for the torque PI controller. See section 2.10.1.2 for details. | V_GenRpm_SP
149 |  |  | 发电机额定转速设定值 | 100 | I32 | 708-709 | rpm | Operational Speed setpoint. This is the rated speed of the turbine. See Operate object for details. | V_OperationSpeedSP
150 |  |  | 最小转矩限值百分比 | 100 | I32 | 710-711 | rpm | Define the dynamic minimum torque to be applied. See section 2.10.1.2 for details | V_TorqueLowerPct
151 |  |  | 最大转矩限值百分比3 | 100 | I32 | 712-713 | rpm | Define the dynamic maximum torque to be applied. See section 2.10.1.2 for details. | V_TorqueUpperPct
152 |  |  | 转矩基值 | 10 | I32 | 714-715 | Nm | Baseline used for the torque PI controllers. See section 2.10.2 for details. | V_TorqueBaseLine
153 |  |  | 转矩基值百分比 | 100 | I16 | 716 | % | Baseline used for the torque PI controllers. See section 2.10.2 for details | V_TorqueBaseLinePct
154 |  |  | 网侧功率 | 1000 | I32 | 717-718 | kw | Active power measured by the control system and exponential averaged by Power Average Time x.xx s p. 246. | V_GridSidePower3SecAvg
155 |  |  | 发电机功率 | 1000 | I32 | 719-720 | kw | Calculated active power on the generator and exponential averaged by Power Average Time x.xx s p. 246. | V_TorqueCalcPower3Sec
156 |  |  | 机组消耗功率 | 1000 | I32 | 721-722 | kw | Estimate of auxiliaries consumption to be compensated by the torque controller in Power Control Mode. See section 2.10.3 for details. | V_PowerLossDynamic
157 |  |  | 机械效率 | 1000 | I32 | 723-724 | / | Efficiency based on lookup table Mech. Efficiency Table p. 241 | V_TorqueMechEfficiency
158 | Inverter |  | 变频器模式 | 1 | I16 | 800 | 字符串 | 1:"Reset" 2:"Stopped" 3:"Run" 4:"Grid Connected" | V_InverterModeTxt
159 |  |  | 发电机转速（编码器） | 10 | I16 | 801 | rpm | Actual speed of the generator. | V_InverterSpeedAct
160 |  |  | 转矩 | 100 | I16 | 802 | % | Actual Generator torque in percentage | V_InverterTorqueAct
161 |  |  | 控制字 | 1 | I16 | 803 | / |  | V_InverterControlWord
162 |  |  | ON(bit 0) | 1 | I16 | 804 | 0/1 |  | V_InverterControlWordOn
163 |  |  | RUN(bit 3) | 1 | I16 | 805 | 0/1 |  | V_InverterControlWordRun
164 |  |  | RESET(bit 7） | 1 | I16 | 806 | 0/1 |  | V_InverterControlWordReset
165 |  |  | 有功功率 | 10 | I16 | 807 | kW | Actual power. | V_InverterPowerAct
166 |  |  | 无功功率 | 10 | I16 | 808 | kvar | Actual reactive power. | V_InverterkVArAct
167 |  |  | 直流母线电压 | 10 | I16 | 809 | V | Mains voltage. | V_InverterUGrid
168 |  |  | 直流母线电流 | 10 | I16 | 810 | A | Line curreunt. | V_InverterIGrid
169 |  |  | 变频器PP温度 | 1 | I16 | 811 | °C | PP temperature in degrees centigrade. | V_InverterPpTemp
170 |  |  | 变频器制动器 | 1 | I16 | 812 | 0/1 | Shows the status of the inverter brealer on 1.4#31 "Inverter Breaker" p. 545 (0 = Error, 1 = OK) | DI_InverterBreaker
171 |  |  | 转矩变化率 | 100 | I16 | 813 | % | Torque setpoint used to control the inverter. | V_InverterTorqueRef
172 |  |  | 相角变化率 | 100 | I16 | 814 | ° |  | V_InverterPhiRef
284 | LVRT |  | LVRT上一次触发时间 | 1 | I64 | 1400-1403 | / | The time stamp of the last LVRT situation | V_TorqueLVRT_DropStartTimeStamp
285 |  |  | LVRT上一次持续时间 | 1 | I32 | 1404-1405 | ms | The duration time of the last LVRT situation | V_TorqueLVRT_DropDurationTime
173 | Generator |  | 发电机转速（主控） | 100 | I32 | 900-901 | rpm | Generator rpm. | AI_GeneratorRpm
174 |  |  | 发电机转速1秒平均值 | 100 | I32 | 902-903 | rpm | Shows the 1 sec. averaged rotor speed | V_GeneratorRpm1Sec
175 |  |  | 发电机转速30秒平均值 | 100 | I32 | 904-905 | rpm | Shows the 30 sec. averaged rotor speed | V_GeneratorRpm30Sec
176 |  |  | 发电机转速10分钟平均值 | 100 | I32 | 906-907 | rpm | Shows the 600 sec. averaged rotor speed | V_GeneratorRpm10Min
177 |  |  | 发电机加热器模式 | 1 | I16 | 908 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenHeatModeText
178 |  |  | 发电机滑环室加热模式 | 1 | I16 | 909 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenSRHeatModeText
179 |  |  | 发电机风扇电机加热模式 | 1 | I16 | 910 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenFansHeatModeText
180 |  |  | 发电机冷却模式 | 1 | I16 | 911 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenCoolerModeText
181 |  |  | 发电机滑环室冷却模式 | 1 | I16 | 912 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenSRCoolerModeText
182 |  |  | 发电机频率 | 1000 | I32 | 913-914 | Hz | Shows the generator speed in Hz. | AI_GeneratorRpmFrq
183 |  |  | 发电机L1绕组温度 | 10 | I16 | 915 | °C | Shows the (G) stator winding L1 temperature. | PT_TempGenCoilL1
184 |  |  | 发电机L2绕组温度 | 10 | I16 | 916 | °C | Shows the (G) stator winding L2 temperature. | PT_TempGenCoilL2
185 |  |  | 发电机L3绕组温度 | 10 | I16 | 917 | °C | Shows the (G) stator winding L3 temperature. | PT_TempGenCoilL3
186 |  |  | 发电机驱动端轴承温度 | 10 | I16 | 918 | °C | Shows the (G) bearing DE temperature. | PT_GeneratorBearingDETemp
187 |  |  | 发电机非驱动端轴承温度 | 10 | I16 | 919 | °C | Shows the (G) bearing NDE temperature. | PT_GeneratorBearingNDETemp
188 |  |  | 发电机加热器状态 | 1 | I16 | 920 | 0/1 | The current condition on output 3.2#14 "Heating Generator" p. 550 (0 = Heating OFF, 1 = Heating ON). | DO_GeneratorHeating
189 |  |  | 发电机滑环室加热器状态 | 1 | I16 | 921 | 0/1 |  | DO_GeneratorSRHeater
190 |  |  | 发电机风扇加热器状态 | 1 | I16 | 922 | 0/1 |  | DO_GeneratorFansHeater
191 |  |  | 发电机加热器反馈 | 1 | I16 | 923 | 0/1 | Heating feedback signal 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK). | DI_FBFuseHeaters
192 |  |  | 发电机前置风扇反馈 | 1 | I16 | 924 | 0/1 | The current condition on output 3.2#16 "Generator Fan Front" p. 550 (0 = Fan OFF, 1 = Fan ON). | DO_GeneratorFanFront
193 |  |  | 发电机顶部风扇反馈 | 1 | I16 | 925 | 0/1 | The current condition on output 3.2#17 "Generator Fan Top" p. 550 (0 = Fan OFF, 1 = Fan ON). | DO_GeneratorFanTop
194 |  |  | 发电机滑环室风扇反馈 | 1 | I16 | 926 | 0/1 |  | DO_GeneratorSRFans
195 |  |  | 发电机风扇断路器反馈 | 1 | I16 | 927 | 0/1 | The current state of the fan feedback on 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK). | DI_FeedbackMCB
196 |  |  | 发电机碳刷报警 | 1 | I16 | 928 | 0/1 | The current state of the brush wear on 3.3#41 "Generator Brush Wear Error" p. 555 (0 = ERROR, 1 = OK). | DI_GeneratorBrushWearError
197 |  |  | 发电机风扇出口温度 | 10 | I16 | 929 | °C | Shows the (G) fan outer temperature. | PT_GeneratorFanOuterTemp
198 |  |  | 发电机滑环室温度 | 10 | I16 | 930 | °C |  | PT_SlipRingTemperature
370 | Power Management |  | 功率控制模式 | 1 | I16 | 2900 | 字符串 | 1:"No Red. Active" 2:"Local, kW" 3:"Local, %" 4:"Remote" 5:"12345678901234567890" 6:"Freq. drop active" 7:"Grid: High Freq." 8:"Low Limit Active" | V_PM_StatusString
371 |  |  | 有功功率设定值 | 1000 | I32 | 2901-2902 | kW | Shows the requested active power production. | V_PM_ActivePowerSetpointW
372 |  |  | 有功功率1秒平均值 | 1000 | I32 | 2903-2904 | kW | Active Power 1s xxxxx.x kW | V_GridRealPower1Sec
373 |  |  | 有功功率10分钟平均值 | 1000 | I32 | 2905-2906 | kW | 10 minute average value of active power production. | V_GridRealPower10Min
374 |  |  | 无功功率设定值 | 1000 | I32 | 2907-2908 | kvar | Shows the requested reactive power. | V_PM_ReactivePowerSetpoint
375 |  |  | 无功功率1秒平均值 | 1000 | I32 | 2909-2910 | kvar | 1 second average value of reactive power production or consumption. | V_GridReactivePower1Sec
376 |  |  | 无功功率10分钟平均值 | 1000 | I32 | 2911-2912 | kvar | 10 minute average value of reactive power production or consumption. | V_GridReactivePower10Min
60 | Brake Disk |  | 制动模式 | 1 | I16 | 400 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"UNKNOWN" | V_BrakeModeText
61 |  |  | 制动类型 | 1 | I16 | 401 | 字符串 | 1:"OPEN" 2:"CLOSE" 3:"AUTO CLOSE" 4:"UNKNOWN" | V_BrakeTypeText
62 |  |  | 制动盘报警 | 1 | I16 | 402 | 0/1 | The current condition on input | DI_BrakePadsOneWornOut
63 |  |  | 液压制动松闸（0=抱闸/1=松闸） | 1 | I16 | 403 | 0/1 | The current condition on input | DO_HydraulicValveBrakerOpen
64 |  |  | 主轴制动释放 | 1 | I16 | 404 | 0/1 | 3.2-51# | TI_RotorBrakeReleased
65 |  |  | 主轴制动抱闸 | 1 | I16 | 405 | 0/1 | 3.2-52# | TI_RotorBrakeLocked
66 |  |  | 主轴转速设定值 | 100 | I32 | 500-501 | rpm | Speed setpoint from Operate to the PID controller. | V_OperateCtrl_RotorSpeedSetpoint
199 | Rotor |  | 主轴转速 | 100 | I32 | 1000-1001 | rpm | Rotor rpm. | AI_RotorRpm
200 |  |  | 主轴轴承1温度 | 10 | I16 | 1002 | °C | The current temperature on PT100 input 3.3#69+ "Spindle Bearing 1" p. 620 | PT_SpindleBearing1
201 |  |  | 主轴轴承2温度 | 10 | I16 | 1003 | °C | The current temperature on PT100 input 3.3#70+ "Spindle Bearing 2" p. 620 | PT_SpindleBearing2
202 |  |  | 主轴软件超速 | 1 | I16 | 1004 | 0/1 | The current condition on input (0 = OK, 1 = Error). | DI_FeedbackRotorOverspeed
203 |  |  | 液压站过滤器堵塞 | 1 | I16 | 1005 | 0/1 | The current condition on input 3.3#46 "Hydraulic Filter Blocked" p. 555 (1 = Error, 0 = OK). Used in status code 441 - Brake pressure p. 270 | DI_HydraulicPressLimitSwitchRotorBrakeLow
204 |  |  | 主轴刹车抱闸 | 1 | I16 | 1006 | 0/1 | The current condition on input 3.2#51 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 85 bar. | TI_RotorBrakeLocked
205 |  |  | 主轴刹车释放 | 1 | I16 | 1007 | 0/1 | The current condition on input 3.2#52 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 10 bar. | TI_RotorBrakeReleased
206 |  |  | 主轴锁定销1释放 | 1 | I16 | 1008 | 0/1 | The current condition on input 3.2#46 "Rotor Unlock 1" p. 551 (1 = Released, 0 = Locked). | DI_RotorLock1
207 |  |  | 主轴锁定销2释放 | 1 | I16 | 1009 | 0/1 | The current condition on input 3.2#47 "Rotor Unlock 2" p. 551 (1 = Released, 0 = Locked) | DI_RotorLock2
208 |  |  | 滑环加热器断路器反馈 | 1 | I16 | 1010 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK). | DI_FBFuseHeaters
209 |  |  | 主轴转速1秒平均值 | 100 | I32 | 1011-1012 | rpm | Shows the 1 sec. averaged rotor speed | V_RotorRpm1Sec
210 |  |  | 主轴转速30秒平均值 | 100 | I32 | 1013-1014 | rpm | Shows the 30 sec. averaged rotor speed | V_RotorRpm30Sec
211 |  |  | 主轴转速10分钟平均值 | 100 | I32 | 1015-1016 | rpm | Shows the 600 sec. averaged rotor speed | V_RotorRpm10Min
212 |  |  | 主轴频率 | 1000 | I32 | 1017-1018 | Hz | Shows the rotor frequency from the sensor | AI_RotorRpmFrq
213 | Gear |  | 齿轮箱润滑油过滤器压力反馈 | 1 | I16 | 1100 | 0/1 | The current gear oil filter pressure 3.3#43 "Gear Oil Presssure Status" p. 618. | DI_GearOilPresssureStatus
214 |  |  | 齿轮箱过滤器堵塞 | 1 | I16 | 1101 | 0/1 | Filter clogged on 3.3#33 "Gear Box Filter Blooding" p. 618 (1 = clogged, 0 = OK). | DI_GearBoxFilterBlooding
215 |  |  | 齿轮箱润滑油油位 | 1 | I16 | 1102 | 0/1 | The current Gear oil level on 3.3#42 "Gear Oil Level/SNK" p. 555 (0=Err, 1=OK). | DI_GearOilLevelSNK
216 |  |  | 齿轮箱润滑油风扇 | 1 | I16 | 1103 | 0/1 | The current condition on output 3.3#8 "Gear Oil Cooling" p. 554 (0=Off, 1=On). | DO_GearOilCoolerHighSpeed
217 |  |  | 齿轮箱润滑油油泵和风扇断路器反馈 | 1 | I16 | 1104 | 0/1 | The current condition on output 3.3#26 "Feedback MCB Gear Box Oil Pump & Gear Oil Cooler" p. 555 (0=Err, 1=Ok). | DI_FeedbackMcbGearOilPumpAndCooler
218 |  |  | 齿轮箱润滑油加热器 | 1 | I16 | 1105 | 0/1 | The current condition on output 3.2#8 "Gear Oil Heating" p. 550 (0=Off, 1=On). | DO_GearOilHeating
219 |  |  | 齿轮箱加热器反馈 | 1 | I16 | 1106 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0=Err, 1=Ok). | DI_FBFuseHeaters
220 |  |  | 齿轮箱润滑油泵高速 | 1 | I16 | 1107 | 0/1 | The current condition on output 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 (0=Off, 1=On). | DO_GearBoxOilPumpHighSpeed
221 |  |  | 齿轮箱润滑油泵低速 | 1 | I16 | 1108 | 0/1 | The current condition on output 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 (0=Off, 1=On). | DO_GearBoxOilPumpLowSpeed
222 |  |  | 齿轮箱风扇电机加热器 | 1 | I16 | 1109 | 0/1 | The current condition on output 3.3#10 "Gear Box Cooler Motor Heater" p. 554 (0=Off, 1=On). This output is set high if 3.3#8 "Gear Oil Cooling" p. 554 is 0. | DO_GearBoxCoolerMotorHeater
223 |  |  | 齿轮箱油泵加热器 | 1 | I16 | 1110 | 0/1 | The current condition on output 3.2#19 "Gear Box Pump Heater" p. 551 (0=Off, 1=On). This output is set high if 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 and 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 both are 0. | DO_GearBoxPumpHeater
224 |  |  | 齿轮箱油温 | 10 | I16 | 1111 | °C | This parameter shows the actual measured temperature of the gear oil on on 3.3#65+ "Gear Box Oil Temp." p. 556. | PT_GearBoxOilTemperature
225 |  |  | 齿轮箱油泵温度 | 10 | I16 | 1112 | °C | The current Gear pump oil temperature on 3.3#66+ "Gear Pump Oil Temp." p. 557. | PT_GearOilPumpTemp
226 |  |  | 齿轮箱轴承1温度 | 10 | I16 | 1113 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557. | PT_GearboxHighSpeedBearing1Temp
227 |  |  | 齿轮箱轴承2温度 | 10 | I16 | 1114 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557. | PT_GearboxHighSpeedBearing2Temp
228 |  |  | 齿轮箱进口油压 | 100 | I32 | 1115-1116 | bar | The current gear box import oil pressure on 3.2#64+ "Gear Box Import Oil Pressure" p. 552. | AI_GearImportOilPressure
229 |  |  | 过滤器进口油压 | 100 | I32 | 1117-1118 | bar | The current filter import oil pressure on 3.2#63+ "Filter Import Oil Pressure" p. 552. | AI_FilterImportOilPressure
230 | Grid |  | 电网电压 | 1 | I32 | 1200-1201 | V | The average of the three measured "Line to neutral"-voltages | AI_GridVoltage
231 |  |  | 电网电流 | 1 | I16 | 1202 | A | The average current for all three lines. | AI_GridCurrent
232 |  |  | 电网频率 | 1000 | I32 | 1203-1204 | Hz | The grid frequency measured by the grid module | V_GridFrequencyLog
233 |  |  | 电网有功功率 | 1000 | I32 | 1205-1206 | kW | The active power measured by the grid module | AI_GridRealPower
234 |  |  | 电网无功功率 | 1000 | I32 | 1207-1208 | kVAr | The reactive power measured by the grid module. | AI_GridReactivePower
235 |  |  | 电网功率因数 | 1000 | I16 | 1209 | / | The power factor calculated by the grid module | AI_GridCosPhi
236 |  |  | 电网L1相电压 | 1 | I32 | 1210-1211 | V | The L1 Voltage "Line to Neutral" measured by the grid module | AI_GridL1Voltage
237 |  |  | 电网L2相电压 | 1 | I32 | 1212-1213 | V | The L2 Voltage "Line to Neutral" measured by the grid module. | AI_GridL2Voltage
238 |  |  | 电网L3相电压 | 1 | I32 | 1214-1215 | V | The L3 Voltage "Line to Neutral" measured by the grid module. | AI_GridL3Voltage
239 |  |  | 电网L1相电流 | 1 | I16 | 1216 | A | The current on L1 measured by the grid module. | AI_GridL1Current
240 |  |  | 电网L2相电流 | 1 | I16 | 1217 | A | The current on L2 measured by the grid module. | AI_GridL2Current
241 |  |  | 电网L3相电流 | 1 | I16 | 1218 | A | The current on L3 measured by the grid module. | AI_GridL3Current
242 |  |  | 电网L1/L2相位角 | 1000 | I32 | 1219-1220 | ° | The phase angle between L1-L2. | AI_GridL1L2PhaseShift
243 |  |  | 电网L1/L3相位角 | 1000 | I32 | 1221-1222 | ° | The phase angle between L1-L3 | AI_GridL1L3PhaseShift
244 |  |  | 有功功率100毫秒平均值 | 1000 | I32 | 1223-1224 | KW |  | V_GridRealPower100ms
245 |  |  | 有功功率1秒平均值 | 1000 | I32 | 1225-1226 | KW |  | V_GridRealPower1Sec
246 |  |  | 有功功率3秒平均值 | 1000 | I32 | 1227-1228 | KW |  | V_GridRealPower3Sec
247 |  |  | 有功功率30秒平均值 | 1000 | I32 | 1229-1230 | KW |  | V_GridRealPower30Sec
248 |  |  | 有功功率10分钟平均值 | 1000 | I32 | 1231-1232 | KW |  | V_GridRealPower10Min
249 |  |  | 无功功率100毫秒平均值 | 1000 | I32 | 1233-1234 | kvar |  | V_GridReactivePower100ms
250 |  |  | 无功功率1秒平均值 | 1000 | I32 | 1235-1236 | kvar |  | V_GridReactivePower1Sec
251 |  |  | 无功功率3秒平均值 | 1000 | I32 | 1237-1238 | kvar |  | V_GridReactivePower3Sec
252 |  |  | 无功功率30秒平均值 | 1000 | I32 | 1239-1240 | kvar |  | V_GridReactivePower30Sec
253 |  |  | 无功功率10分钟平均值 | 1000 | I32 | 1241-1242 | kvar |  | V_GridReactivePower10Min
254 |  |  | L1相电压互感器变比 | 1000 | I32 | 1243-1244 | / |  | V_GridL1VoltageGain
255 |  |  | L2相电压互感器变比 | 1000 | I32 | 1245-1246 | / |  | V_GridL2VoltageGain
256 |  |  | L3相电压互感器变比 | 1000 | I32 | 1247-1248 | / |  | V_GridL3VoltageGain
257 |  |  | L1相电流互感器变比 | 1000 | I32 | 1249-1250 | / |  | V_GridL1CurrentGain
258 |  |  | L2相电流互感器变比 | 1000 | I32 | 1251-1252 | / |  | V_GridL2CurrentGain
259 |  |  | L3相电流互感器变比 | 1000 | I32 | 1253-1254 | / |  | V_GridL3CurrentGain
260 |  |  | 电网L1相峰值电压 | 1 | I32 | 1255-1256 | V | The highest voltage measured on L1 based on "Line to Neutral". | S_GridL1VoltagePeak
261 |  |  | 电网L1相峰值电压发生时间 | 1 | I64 | 1257-1260 | / | This menuline shows the timestamp for when the voltage peak, see Peak Volt. L1 x V p. 332, occured. | B_PeakTimeGridVoltL1
262 |  |  | 电网L2相峰值电压 | 1 | I32 | 1261-1262 | V | The highest voltage measured on L2 based on "Line to Neutral". | S_GridL2VoltagePeak
263 |  |  | 电网L2相峰值电压发生时间 | 1 | I64 | 1263-1266 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L2 x V p. 332, occured. | B_PeakTimeGridVoltL2
264 |  |  | 电网L3相峰值电压 | 1 | I32 | 1267-1268 | V | The highest voltage measured on L3 based on "Line to Neutral". | S_GridL3VoltagePeak
265 |  |  | 电网L3相峰值电压发生时间 | 1 | I64 | 1269-1272 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L3 x V p. 332, occured. | B_PeakTimeGridVoltL3
266 |  |  | 电网L1相峰值电流 | 1 | I32 | 1273-1274 | A | The highest current measured on L1 | S_GridL1CurrentPeak
267 |  |  | 电网L1相峰值电流发生时间 | 1 | I64 | 1275-1278 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L1 x A p. 332, occured. | B_PeakTimeGridCurrentL1
268 |  |  | 电网L2相峰值电流 | 1 | I32 | 1279-1280 | A | The highest current measured on L2. | S_GridL2CurrentPeak
269 |  |  | 电网L2相峰值电流发生时间 | 1 | I64 | 1281-1284 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L2 x A p. 333, occured. | B_PeakTimeGridCurrentL2
270 |  |  | 电网L3相峰值电流 | 1 | I32 | 1285-1286 | A | The highest current measured on L3 | S_GridL3CurrentPeak
271 |  |  | 电网L3相峰值电流发生时间 | 1 | I64 | 1287-1290 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L3 x A p. 333, occured. | B_PeakTimeGridCurrentL3
272 |  |  | 电网L1相最大正向矢量波动值 | 1000 | I32 | 1291-1292 | ° | The highest positive peak vector surge on L1. | S_GridL1VectorSurgePositivePeak
273 |  |  | 电网L1相最大正向矢量波动值发生时间 | 1 | I64 | 1293-1296 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L1 x.x ° p. 333, has occured. | B_PeakTimeGridVSPosL1
274 |  |  | 电网L2相最大正向矢量波动值 | 1000 | I32 | 1297-1298 | ° | The highest positive peak vector surge on L2. | S_GridL2VectorSurgePositivePeak
275 |  |  | 电网L2相最大正向矢量波动值发生时间 | 1 | I64 | 1299-1302 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L2 x.x ° p. 333, has occured. | B_PeakTimeGridVSPosL2
276 |  |  | 电网L3相最大正向矢量波动值 | 1000 | I32 | 1303-1304 | ° | The highest positive peak vector surge on L3 | S_GridL3VectorSurgePositivePeak
277 |  |  | 电网L3相最大正向矢量波动值发生时间 | 1 | I64 | 1305-1308 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L3 x.x ° p. 334, has occured | B_PeakTimeGridVSPosL3
278 |  |  | 电网L1相最大负向矢量波动值 | 1000 | I32 | 1309-1310 | ° | The highest negative peak vector surge on L1 | S_GridL1VectorSurgeNegativePeak
279 |  |  | 电网L1相最大负向矢量波动值发生时间 | 1 | I64 | 1311-1314 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L1 x.x ° p. 334, has occured. | B_PeakTimeGridVSNegL1
280 |  |  | 电网L2相最大负向矢量波动值 | 1000 | I32 | 1315-1316 | ° | The highest negative peak vector surge on L2 | S_GridL2VectorSurgeNegativePeak
281 |  |  | 电网L2相最大负向矢量波动值发生时间 | 1 | I64 | 1317-1320 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L2 x.x ° p. 334, has occured. | B_PeakTimeGridVSNegL2
282 |  |  | 电网L3相最大负向矢量波动值 | 1000 | I32 | 1321-1322 | ° | The highest negative peak vector surge on L3. | S_GridL3VectorSurgeNegativePeak
283 |  |  | 电网L3相最大负向矢量波动值发生时间 | 1 | I64 | 1323-1326 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L3 x.x ° p. 334, has occured. | B_PeakTimeGridVSNegL3
286 | Hydraulic |  | 液压站状态 | 1 | I16 | 1500 | 字符串 | 1:"Blocked" 2:"Service On" 3:"Service Off" 4:"Auto" | V_HydraulicPumpStateTxt
287 |  |  | 液压站油泵状态 | 1 | I16 | 1501 | 0/1 | The current condition on 3.2#7 "Hydraulic pump" p. 550 (0 = Off, 1 = On). | DO_HydraulicPump
288 |  |  | 液压站油泵过载（0=Error/1=OK） | 1 | I16 | 1502 | 0/1 | The current condition on input 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK). | DI_FeedbackMCB
289 |  |  | 液压站油位 | 1 | I16 | 1503 | 0/1 | The current condition on input 3.3#38 "Hydraulic Oil Level" p. 555 (0 = Low, 1 = OK). | DI_HydraulicOilLevel
290 |  |  | 液压站温度高（>70） | 1 | I16 | 1504 | 0/1 | The current condition on input 3.3#28 "Hydraulic Temp. High (>=70 °C)" p. 555 (0 = OK, 1 = High). | DI_HydraulicTempHighGreaterThan70
291 |  |  | 液压站系统压力（1=OK/0=Low） | 1 | I16 | 1505 | 0/1 | The current pressure condition on input 3.3#44 "Hydraulic System Pressure Motor Start (Position 40)" p. 555 (1 = OK, 0 = Low). | DI_HydraulicSystemPressureMotorStart
292 |  |  | 液压站系统压力（1=OK/0=High） | 1 | I16 | 1506 | 0/1 | The current pressure condition on input 3.3#45 "" p. 555 (1 = OK, 0 = High). | DI_HydraulicSystemPressure
293 |  |  | 液压站压力 | 100 | I32 | 1507-1508 | bar | The current condition on the scaled input 3.2#62+ "Hydraulic Pressure" p. 552 (in bar). | AI_HydraulicPressure
294 | PT100 |  | 反馈点1.4.65信号错误 | 1 | I16 | 1600 | 0/1 |  | V_TowerControlBoxControlTemp_Err
295 |  |  | 反馈点1.4.66信号错误 | 1 | I16 | 1601 | 0/1 |  | V_TowerBaseTemp_Err
296 |  |  | 反馈点1.4.67信号错误 | 1 | I16 | 1602 | 0/1 |  | V_TransformerTemp1_Err
297 |  |  | 反馈点1.4.68信号错误 | 1 | I16 | 1603 | 0/1 |  | V_TransformerTemp2_Err
298 |  |  | 反馈点1.4.69信号错误 | 1 | I16 | 1604 | 0/1 |  | V_OutdoorTemperature_Err
299 |  |  | 反馈点3.2.65信号错误 | 1 | I16 | 1605 | 0/1 |  | V_TempNacelle_Err
300 |  |  | 反馈点3.2.66信号错误 | 1 | I16 | 1606 | 0/1 |  | V_ControlPanelTemp_Err
301 |  |  | 反馈点3.2.67信号错误 | 1 | I16 | 1607 | 0/1 |  | V_SlipRingTemp_Err
302 |  |  | 反馈点3.2.68信号错误 | 1 | I16 | 1608 | 0/1 |  | V_TempGenCoilL1_Err
303 |  |  | 反馈点3.2.69信号错误 | 1 | I16 | 1609 | 0/1 |  | V_TempGenCoilL2_Err
304 |  |  | 反馈点3.2.70信号错误 | 1 | I16 | 1610 | 0/1 |  | V_TempGenCoilL3_Err
305 |  |  | 反馈点3.2.71信号错误 | 1 | I16 | 1611 | 0/1 |  | V_TempGenBearingDE_Err
306 |  |  | 反馈点3.2.72信号错误 | 1 | I16 | 1612 | 0/1 |  | V_TempGenBearingNDE_Err
307 |  |  | 反馈点3.3.65信号错误 | 1 | I16 | 1613 | 0/1 |  | V_GearOilTemperature_Err
308 |  |  | 反馈点3.3.66信号错误 | 1 | I16 | 1614 | 0/1 |  | V_GearOilPumpTemp_Err
309 |  |  | 反馈点3.3.67信号错误 | 1 | I16 | 1615 | 0/1 |  | V_GearboxHighSpeedBearing1Temp_Err
310 |  |  | 反馈点3.3.68信号错误 | 1 | I16 | 1616 | 0/1 |  | V_GearboxHighSpeedBearing2Temp_Err
311 |  |  | 反馈点3.3.69信号错误 | 1 | I16 | 1617 | 0/1 |  | V_SpindleBearingOne_Err
312 |  |  | 反馈点3.3.70信号错误 | 1 | I16 | 1618 | 0/1 |  | V_SpindleBearingTwo_Err
313 |  |  | 反馈点3.3.72信号错误 | 1 | I16 | 1619 | 0/1 |  | V_GenFanOutterTemp_Err
314 | 4-20mA |  | 反馈点3.2.62信号错误 | 1 | I16 | 1700 | 0/1 |  | V_HydraulicPressureCurrent_Err
315 |  |  | 反馈点3.2.63信号错误 | 1 | I16 | 1701 | 0/1 |  | V_FilterImportOilPressureCurrent_Err
316 |  |  | 反馈点3.3.61信号错误 | 1 | I16 | 1702 | 0/1 |  | V_WindDirectionOneCurrent_Err
317 |  |  | 反馈点3.3.62信号错误 | 1 | I16 | 1703 | 0/1 |  | V_WindDirectionTwoCurrent_Err
318 | Anemometer |  | 3秒平均风速 | 100 | I16 | 1800 | m/s | This shows the 3 sec. averaged wind speed. | V_WindSpeed3Sec
319 |  |  | 30秒平均风速 | 100 | I16 | 1801 | m/s | This shows the 30 sec. averaged wind speed | V_WindSpeed30Sec
319+ |  |  | 10分钟平均风速 | 100 | I16 | 1802 | m/s |  | V_WindSpeed10Min | 5月16日新增
320 |  |  | 当前使用的风速仪 | 1 | I16 | 1803 | / | This parameter shows the active anemometer. | V_WindSpeedActive
321 |  |  | 风速 | 100 | I16 | 1804 | m/s | This parameter shows the wind speed from the selected anemometer. | AI_WindSpeed
322 |  |  | 风速仪1实际反馈值 | 1000 | I32 | 1805-1806 | Hz |  | HSI_WindSpeedOne_Frq
323 |  |  | 风速仪2实际反馈值 | 1000 | I32 | 1807-1808 | Hz |  | HSI_WindSpeedTwo_Frq
324 | Wind Vane |  | 3秒平均风向 | 10 | I16 | 1900 | ° | Shows the 3 seconds averaged wind direction from the selected windvane. | V_WindVaneDirection3Sec
325 |  |  | 30秒平均风向 | 10 | I16 | 1901 | ° | Shows the 30 seconds averaged wind direction from the selected wind vane | V_WindVaneDirection30Sec
325+ |  |  | 10分钟平均风速 | 10 | I16 | 1092 | ° |  | V_WindDirection10M | 5月16日新增
326 |  |  | 风向 | 10 | I16 | 1903 | ° | Shows the wind direction from the active wind vane. | AI_WindVaneDirection
327 |  |  | 机舱相对风向偏移量 | 10 | I16 | 1904 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned according to the correct wind direction. | V_RelaWindVaneDirection3Sec
328 |  |  | 机舱相对正北角度 | 10 | I16 | 1905 | ° | Shows the position of the nacelle seen in proportion to a circle where 0°is North. | V_NacelleDirection
329 |  |  | 当前使用的风向仪 | 1 | I32 | 1906-1907 | / | Shows which of the two wind vanes is currently active | V_WindVaneActiveVane
330 |  |  | 风向仪1相对正北角度 | 10 | I16 | 1908 | ° | Shows the wind direction seen in proportion to a circle where 0°is North. | V_WindDirection1
331 |  |  | 风向仪2相对正北角度 | 10 | I16 | 1909 | ° | Shows the wind direction 2 seen in proportion to a circle where 0°is North. | V_WindDirection2
332 |  |  | 风向仪1相对机舱角度 | 10 | I16 | 1910 | ° | Shows the wind vane 1 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection1
333 |  |  | 风向仪2相对机舱角度 | 10 | I16 | 1911 | ° | Shows the wind vane 2 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection2
334 |  |  | 风向仪1实际反馈值 | 1000 | I16 | 1912 | mA |  | AI_WindDirection1Current
335 |  |  | 风向仪2实际反馈值 | 1000 | I16 | 1913 | mA |  | AI_WindDirection2Current
336 | Outdoor |  | 测风仪加热器状态 | 1 | I16 | 2000 | 0/1 | The current condition on output 3.2#15 "Heating wind sensor" p. 550 (0 = Off, 1 = On). | DO_HeatingWindSensor
337 |  |  | 环境温度 | 10 | I16 | 2001 | °C | The measured environment temperature on input 1.4#69+ "Enviroment Temperature" p. 547. | PT_OutdoorTemp
338 | Lightning |  | 塔基柜内浪涌保护器 | 1 | I16 | 2100 | 0/1 | The current state of input 1.4#29 "Surge Protection (Tower Base)" p. 545. | DI_SurgeProtectionTowerBase
340 | Transformer |  | 箱变温度1 | 10 | I16 | 2200 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546). | PT_TransformerTemp1
341 |  |  | 箱变温度2 | 10 | I16 | 2201 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#68+ "Transfomer Temp. 2" p. 547). | PT_TransformerTemp2
342 |  |  | 35KV开关状态（0=OFF/1=ON） | 1 | I16 | 2202 | 0/1 | Shows the status of the 35 kV switch (Terminal 1.4#33 "Measuring open/close of the 35 kV switch" p. 545, 0 = OFF, 1 = ON). | DI_MeasOpenClose35kVSwitch
343 |  |  | 690V开关状态（0=OFF/1=ON） | 1 | I16 | 2203 | 0/1 | Shows the status of the 690 volt switch (Terminal 1.4#34 "Measuring open/close of the 0.69 kV switch" p. 545, 0 = OFF, 1 = ON). | DI_MeasOpenClose690VSwitch
344 |  |  | 箱变温度高 | 1 | I16 | 2204 | 0/1 |  | DI_TransformerTempHigh
345 |  |  | 箱变油位状态 | 1 | I16 | 2205 | 0/1 |  | DI_TransformerOilLevel
350 | Tower Base |  | 塔基温度 | 10 | I16 | 2400 | °C | Tower base temperature (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546) | PT_TowerBaseTemp
351 |  |  | 塔基烟雾报警 | 1 | I16 | 2401 | 0/1 |  | DI_TowerBaseSmokeDetection
352 | Ups |  | UPS通讯OK | 1 | I16 | 2500 | 0/1 | Communication status | V_UPSCommunicationOk
353 |  |  | UPS剩余时间 | 1 | I32 | 2501-2502 | s | The measured UPS remaining operation time with nominel load. The value is received through the serial connection to the UPS. In case of any communication error, the UPS remaining time is forced to zero. | V_UPSRemainingTime
339 |  |  | 机舱柜内浪涌保护器 | 1 | I16 | 2101 | 0/1 | The current state of input 3.3#50 "Surge Protection Nacelle" p. 555. | DI_SurgeProtectionTowerBase
346 | Air Pressure |  | 当前大气压力 | 1 | I16 | 2300 | mbar |  | V_AirPressure
347 |  |  | 1秒平均气压 | 1 | I16 | 2301 | mbar |  | V_AirPressure1Sec
348 |  |  | 30秒平均气压 | 1 | I16 | 2302 | mbar |  | V_AirPressure30Sec
349 |  |  | 10分钟平均气压 | 1 | I16 | 2303 | mbar |  | V_AirPressure10Min
377 | Vibration monitoring |  | 振动传感器1通道1值 | 1000 | I16 | 3000 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1 | V_WP4084No1VibOne
378 |  |  | 振动传感器1通道2值 | 1000 | I16 | 3001 | G | Shows the vibration level in sensor WP4084 No. 1, channel 2 | V_WP4084No1VibTwo
379 |  |  | 振动传感器1通道1+2值 | 1000 | I16 | 3002 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1 + channel 2 | V_WP4084No1VibOnePlusTwo
380 |  |  | 振动传感器1通道1状态 | 1 | I16 | 3003 | 0/1 | Shows the status of the WP4084 No. 1, channel 1 (0 = Ok, 1 = Vibration alarm, 2 = Selftest error). See section 2.39.5 for further details on sensor monitoring. | V_WP4084No1SensorOne
381 |  |  | 振动传感器1通道2状态 | 1 | I16 | 3004 | 0/1 | Shows the status of the sensor selftest (0 = Idle, 1 = Active). See section 2.39.4 for further details on sensor selftest. | V_WP4084No1SensorTwo
382 |  |  | 软件自检类型 | 1 | I16 | 3005 | 0/1 | Shows the selftest failure delay used by the sensor selftest software. (0 = 24 hours, 1 = 24 minutes). See section 2.39.4 for further details on sensor selftest. | V_WP4084No1SensorTest
383 |  |  | 振动传感器1通讯状态 | 1 | I16 | 3006 | 字符串 | 1:"Disabled" 2:"Error" 3:"Ok" | V_WP4084No1CommunicationTxt
384 | Flight Warning Light |  | 航空灯供电OK | 1 | I16 | 3100 | 0/1 | The current condition on input 3.3#36 "Supply Obstruction Lights 1 & 2 230V" p. 555 (0 = Error, 1 = Ok). | DI_FlightWarningLightSupplyOk
385 |  |  | 航空灯故障 | 1 | I16 | 3101 | 0/1 | The current condition on input 3.3#37 "Flight Warning Error" p. 555 (1 = Error, 0 = Ok). | DI_FlightWarningLightOk
354 | Lubrication |  | 发电机润滑油泵状态 | 1 | I16 | 2600 | 0/1 |  | DO_Lubrication_GeneratorBearingPump
355 |  |  | 轮毂轴承润滑油油位 | 1 | I16 | 2601 | 0/1 | The current condition on input 3.3#39 "Pitch Bearing Inner Ring Lubrication Grease Level" p. 555 (0 = Empty, 1 = OK). | DI_PitchBearInRingLubriGreaseLvl
356 |  |  | 轮毂轴承润滑油堵塞 | 1 | I16 | 2602 | 0/1 | The current condition on input 3.3#40 "Pitch Bearing Inner Ring Lubrication Blinding" p. 555 (Pulsing = OK, Not pulsing = Err). | DI_PitchBearInRingLubriBlind
357 |  |  | 轮毂润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2603 | 0/1 | The current condition on output 3.2#20 "Lubrication Pump Pitch System (Outer Ring)" p. 551 (0 = OFF, 1 = ON). | DO_LubriPumpPitchSystemRingIn
358 |  |  | 机舱轴承润滑油油位 | 1 | I16 | 2604 | 0/1 |  | DI_RotorBearLubriGreaseLvl
359 |  |  | 机舱轴承润滑油堵塞 | 1 | I16 | 2605 | 0/1 | The current condition on input 3.2#43 "Yaw Bear Lubrication Blinding" p. 551 (Pulsing = OK, Not pulsing = Err) | TI_YawBearLubricationBlind
360 |  |  | 机舱润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2606 | 0/1 | The current condition on output 3.3#9 "Yaw Lubrication Pump 1" p. 554 (0 = OFF, 1 = ON). | DO_YawLubricationPump1
361 | Nacelle |  | 机舱温度 | 10 | I16 | 2700 | °C | Nacelle temperature on PT100 input 3.2#65+ "Nacelle Temperature" p. 553. | PT_NacelleTemp
362 |  |  | 机舱风扇状态 | 1 | I16 | 2701 | 0/1 | Nacelle fan ON/OFF (output 3.2#18 "Nacelle Fan 1 & 2" p. 550). | DO_AirStreamSystem1_2
363 |  |  | 机舱风扇断路器反馈 | 1 | I16 | 2702 | 0/1 | Nacelle fan MCB FB ON/OFF (input 3.3#27 "Feedback MCB" p. 555). | DI_FeedbackMCB
364 |  |  | 机舱加热器1+2状态 | 1 | I16 | 2703 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF" | V_NacelleHeater1_2_Txt
365 |  |  | 机舱加热器3+4状态 | 1 | I16 | 2704 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF" | V_NacelleHeater3_4_Txt
366 |  |  | 机舱烟雾报警 | 1 | I16 | 2705 | 0/1 |  | DI_NacelleSmokeDetection
367 | Panels |  | 机舱柜温度 | 10 | I16 | 2800 | °C | Shows the status of the nacelle control panel temperature (Terminal 3.2#66+ "Nacelle Panel Temperature" p. 553). | PT_NacelleControlPanelTemp
368 |  |  | 塔基柜温度 | 10 | I16 | 2801 | °C | Shows the temperature of the tower base panel (Terminal 1.4#65+ "Tower Base Panel Temperature" p. 546). | PT_TowerBasePanelTemp
369 |  |  | 以太网开关OK | 1 | I16 | 2802 | 0/1 | Shows the status of the ethernet switch ES100 (Terminal 1.4#32 "Ethernet Switch ES100 OK" p. 545) | DI_EthernetSwitchOk
393 | 机组部件运行统计 |  | 顺时针偏航激活时长 | 10 | I64 | 3300-3303 | 小时 |  | DO_YawMotorCw
394 |  |  | 顺时针偏航激活次数 | 1 | I64 | 3304-3307 | 次
395 |  |  | 逆时针偏航激活时长 | 10 | I64 | 3308-3311 | 小时 |  | DO_YawMotorCcw
396 |  |  | 逆时针偏航激活次数 | 1 | I64 | 3312-3315 | 次
397 |  |  | 偏航电机激活时长 | 10 | I64 | 3316-3319 | 小时 |  | V_SumYawMotorActive
398 |  |  | 偏航电机激活次数 | 1 | I64 | 3320-3323 | 次
399 |  |  | 刹车盘抱闸时长 | 10 | I64 | 3324-3327 | 小时 |  | V_SumBrakeDisk
400 |  |  | 刹车盘抱闸次数 | 1 | I64 | 3328-3331 | 次
401 |  |  | 刹车盘施放时长 | 10 | I64 | 3332-3335 | 小时 |  | V_SumBrakeFree
402 |  |  | 刹车盘释放次数 | 1 | I64 | 3336-3339 | 次
403 |  |  | 发电机加热器工作时长 | 10 | I64 | 3340-3343 | 小时 |  | DO_GeneratorHeating
404 |  |  | 发电机加热器工作次数 | 1 | I64 | 3344-3347 | 次
405 |  |  | 发电机滑环室加热器工作时长 | 10 | I64 | 3348-3351 | 小时 |  | DO_GeneratorSRHeater
406 |  |  | 发电机滑环室加热器工作次数 | 1 | I64 | 3352-3355 | 次
407 |  |  | 发电机风扇电机加热器工作时长 | 10 | I64 | 3356-3359 | 小时 |  | DO_GeneratorFansHeater
408 |  |  | 发电机风扇电机加热器工作次数 | 1 | I64 | 3360-3363 | 次
409 |  |  | 发电机滑环室风扇工作时长 | 10 | I64 | 3364-3367 | 小时 |  | DO_GeneratorSRFans
410 |  |  | 发电机滑环室风扇工作次数 | 1 | I64 | 3368-3371 | 次
411 |  |  | 发电机风扇1工作时长 | 10 | I64 | 3372-3375 | 小时 |  | DO_GeneratorFanFront
412 |  |  | 发电机风扇1工作次数 | 1 | I64 | 3376-3379 | 次
413 |  |  | 发电机风扇2工作时长 | 10 | I64 | 3380-3383 | 小时 |  | DO_GeneratorFanTop
414 |  |  | 发电机风扇2工作次数 | 1 | I64 | 3384-3387 | 次
415 |  |  | 齿轮箱润滑油加热器工作时长 | 10 | I64 | 3388-3391 | 小时 |  | DO_GearOilHeating
416 |  |  | 齿轮箱润滑油加热器工作次数 | 1 | I64 | 3392-3395 | 次
417 |  |  | 齿轮箱风扇工作时长 | 10 | I64 | 3396-3399 | 小时 |  | DO_GearOilCoolerHighSpeed
418 |  |  | 齿轮箱风扇工作次数 | 1 | I64 | 3400-3403 | 次
419 |  |  | 齿轮箱油泵低速工作时长 | 10 | I64 | 3404-3407 | 小时 |  | DO_GearBoxOilPumpLowSpeed
420 |  |  | 齿轮箱油泵低速工作次数 | 1 | I64 | 3408-3411 | 次
421 |  |  | 齿轮箱油泵高速工作时长 | 10 | I64 | 3412-3415 | 小时 |  | DO_GearBoxOilPumpHighSpeed
422 |  |  | 齿轮箱油泵高速工作次数 | 1 | I64 | 3416-3419 | 次
423 |  |  | 液压站油泵工作时长 | 10 | I64 | 3420-3423 | 小时 |  | DO_HydraulicPump
424 |  |  | 液压站油泵工作次数 | 1 | I64 | 3424-3427 | 次
425 |  |  | 测风仪加热器工作时长 | 10 | I64 | 3428-3431 | 小时 |  | DO_HeatingWindSensor
426 |  |  | 测风仪加热器工作次数 | 1 | I64 | 3432-3435 | 次
| 电量统计 |  | 总发电量 | 1 | I64 | 3500-3503 | kWh |  | S_TotalProduction
|  |  | 总用电量 | 1 | I64 | 3504-3507 | kWh
|  |  | 日发电量 | 1 | I64 | 3508-3511 | kWh
|  |  | 日用电量 | 1 | I64 | 3512-3515 | kWh
|  |  | 周发电量 | 1 | I64 | 3516-3519 | kWh
|  |  | 周用电量 | 1 | I64 | 3520-3523 | kWh
|  |  | 月发电量 | 1 | I64 | 3524-3527 | kWh
|  |  | 月用电量 | 1 | I64 | 3528-3531 | kWh
|  |  | 年发电量 | 1 | I64 | 3532-3535 | kWh
|  |  | 年用电量 | 1 | I64 | 3536-3539 | kWh
| 时间统计 |  | 总发电时间 | 10 | I64 | 3540-3543 | 小时 |  | S_TotalOperation
|  |  | 日发电时间 | 10 | I64 | 3544-3547 | 小时
|  |  | 周发电时间 | 10 | I64 | 3548-3551 | 小时
|  |  | 月发电时间 | 10 | I64 | 3552-3555 | 小时
|  |  | 年发电时间 | 10 | I64 | 3556-3559 | 小时
|  |  | 总运行时间 | 10 | I64 | 3560-3563 | 小时 |  | S_Operate
|  |  | 日运行时间 | 10 | I64 | 3564-3567 | 小时
|  |  | 周运行时间 | 10 | I64 | 3568-3571 | 小时
|  |  | 月运行时间 | 10 | I64 | 3572-3575 | 小时
|  |  | 年运行时间 | 10 | I64 | 3576-3579 | 小时
|  |  | 总停机时间 | 10 | I64 | 3580-3583 | 小时 |  | S_OperationStopped
|  |  | 日停机时间 | 10 | I64 | 3584-3587 | 小时
|  |  | 周停机时间 | 10 | I64 | 3588-3591 | 小时
|  |  | 月停机时间 | 10 | I64 | 3592-3595 | 小时
|  |  | 年停机时间 | 10 | I64 | 3596-3599 | 小时
|  |  | 总启动风速时间 | 10 | I64 | 3600-3603 | 小时 |  | S_Startwind
|  |  | 日启动风速时间 | 10 | I64 | 3604-3607 | 小时
|  |  | 周启动风速时间 | 10 | I64 | 3608-3611 | 小时
|  |  | 月启动风速时间 | 10 | I64 | 3612-3615 | 小时
|  |  | 年启动风速时间 | 10 | I64 | 3616-3619 | 小时
| 风速统计 |  | 总平均风速 | 10 | I32 | 3620-3621 | m/s |  | S_WindspeedAvg
|  |  | 日平均风速 | 10 | I32 | 3622-3623 | m/s
|  |  | 周平均风速 | 10 | I32 | 3624-3625 | m/s
|  |  | 月平均风速 | 10 | I32 | 3626-3627 | m/s
|  |  | 年平均风速 | 10 | I32 | 3628-3629 | m/s
| 可利用率统计 |  | 总可利用率 | 100 | F32 | 3630-3631 | % |  | Availability
|  |  | 日可利用率 | 100 | F32 | 3632-3633 | %
|  |  | 周可利用率 | 100 | F32 | 3634-3635 | %
|  |  | 月可利用率 | 100 | F32 | 3636-3637 | %
|  |  | 年可利用率 | 100 | F32 | 3638-3639 | %

## PPM
序号 | 目录 |  | 名称 | Config |  |  | 单位 | 描述 | 变量名
|  |  |  | 倍数 | 数据类型 | 地址
| Turbine to PPM | 有功 | 有功握手信号 | 1 | I16 | 4000 | - |  | V_SentToPPMAPCount
|  |  | 有功状态 | 1 | I16 | 4001 | - |  | V_APStateToPPM
|  |  | 有功3秒均值 | 1 | I32 | 4002-4003 | W |  | V_GridRealPower3Sec
|  |  | 当前可利用功率 | 1 | I32 | 4004-4005 | W |  | V_AvailablePowerToPPM
|  |  | 当前可利用功率10min平均值 | 1 | I32 |  | W
|  |  | 额定功率 | 1 | I32 | 4006-4007 | W |  | P_RatedPower
|  |  | 当前有功限值 | 1 | I32 | 4008-4009 | W |  | V_PM_ActivePowerSetpointW
|  |  | 累计有功发电量 | 1 | I32 | 4010-4011 | kWh |  | S_TotalProduction
|  |  | 累计发电时间 | 1 | I32 | 4012-4013 | s |  | S_TotalOperation
|  |  | 当前风速3秒均值 | 1 | I16 | 4014 | 0.1m/s |  | V_WindSpeed3Sec
|  |  | PPM有功通讯中断间隔限值 | 1 | I32 | 4015-4016 | S | 该值为设定PPM有功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5007故障 | P_APComChangeTime
|  |  | 预留 |  | I32 | 4017-4018
|  |  | 预留 |  | I32 | 4019-4020
|  | 无功 | 无功握手信号 | 1 | I16 | 4021 | - |  | V_SentToPPMRPCount
|  |  | 无功状态 | 1 | I16 | 4022 | - |  | V_RPStateToPPM
|  |  | 无功3秒均值 | 1 | I32 | 4023-4024 | kVar |  | V_GridReactivePower3Sec
|  |  | PPM无功通讯中断间隔限值 | 1 | I32 | 4025-4026 | S | 该值为设定PPM无功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5008故障 | P_RPComChangeTime
|  |  | 当前无功限值 | 1 | I32 | 4027-4028 | Var |  | V_PM_ReactivePowerSetpoint
| PPM to Turbine | 有功 | PPM有功握手信号 | 1 | I16 | 4029 | - |  | V_APCountFromPPM
|  |  | PPM有功控制模式 | 1 | I16 | 4030 | - |  | V_APStateFromPPM
|  |  | 有功设定值 | 1 | I32 | 4031-4032 | W |  | V_ActivePowerSetpoint
|  |  | 预留 |  | I32 | 4033-4034
|  | 无功 | PPM无功握手信号 | 1 | I16 | 4035 | - |  | V_RPCountFromPPM
|  |  | PPM无功控制模式 | 1 | I16 | 4036 | - |  | V_RPStateFromPPM
|  |  | 无功设定值 | 1 | I32 | 4037-4038 | Var |  | V_ReactivePowerSetpoint
|  |  | 预留 |  | I32 | 4039-4040
|  |  | 预留 |  | I32 | 4041-4042

## 安全链
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 1 | Safety Chain | 安全链状态 | 1 | I16 | 100 | 字符串 | 1:"EStop Error" 2:"SC1 Error" 3:"SC2 Error" 4:"Safety Ok"
| 2 |  | 安全链故障 | 1 | I16 | 101 | 字符串 | 1:"Detecting..." 2:"Emergency Stop Nacelle Ext." 3:"Emergency Stop Nacelle" 4:"Emergency Stop Tower Base" 5:"EStop Awaiting reset" 6:"SafetyChain MCB" 7:"Vibration" 8:"WP2035 (R) Overspeed" 9:"WP2035 (G) Overspeed" 10:"SC1 Awaiting reset" 11:"Manual Safety Stop Nacelle" 12:"WP4000 Controller relay" 13:"SC2 Awaiting reset" 14:"None"
| 3 |  | 安全链复位模式 | 1 | I16 | 102 | 字符串 | 1:"OFF" 2:"MANUAL" 3:"AUTOMATIC" 4:"ON" 5:"UNKNOWN"
| 4 |  | 上电复位模式 | 1 | I16 | 103 | 字符串 | 1:"Done" 2:"Executing" 3:"None" 4:"Pending"
| 5 |  | 机舱急停按钮状态 | 1 | I16 | 104 | 0/1 | The current condition on input
| 6 |  | 机舱柜急停按钮状态 | 1 | I16 | 105 | 0/1 | The current condition on input
| 7 |  | 塔基急停按钮状态 | 1 | I16 | 106 | 0/1 | The current condition on input
| 8 |  | 急停继电器状态 | 1 | I16 | 107 | 0/1 | The current condition on input
1 | 9 |  | 安全链总状态 | 1 | I16 | 108 | 0/1 | The current condition on input
1 | 10 |  | 振动开关状态 | 1 | I16 | 109 | 0/1 | The current condition on input
1 | 11 |  | 安全链继电器1状态 | 1 | I16 | 110 | 0/1 | The current condition on input
1 | 12 |  | WP2035主轴超速模块状态 | 1 | I16 | 111 | 0/1 | Shows the rotor wp2035 overspeed detection, the current condition on input
1 | 13 |  | WP2035发电机超速模块状态 | 1 | I16 | 112 | 0/1 | Shows the generator wp2035 overspeed detection, the current condition on input
| 14 |  | 机舱柜安全停机 | 1 | I16 | 113 | 0/1 | The current condition on input
| 15 |  | WP4100安全链输入信号 | 1 | I16 | 114 | 0/1 | The current condition on input
| 16 |  | WP4100安全链输出信号 | 1 | I16 | 115 | 0/1 | The current condition on input
1 | 17 |  | 变桨安全链状态 | 1 | I16 | 116 | 0/1 | The current condition on input
1 | 18 |  | 安全链继电器2状态 | 1 | I16 | 117 | 0/1 | The current condition on input
| 19 |  | 塔基手动停机 | 1 | I16 | 118 | 0/1 | The current condition on input
| 20 |  | 机舱手动停机 | 1 | I16 | 119 | 0/1 | The current condition on input
| 21 |  | 手动停止顺时针偏航 | 1 | I16 | 120 | 0/1 | The current condition on input
| 22 |  | 手动停止逆时针偏航 | 1 | I16 | 121 | 0/1 | The current condition on input
| 23 |  | 本地复位安全链信号 | 1 | I16 | 122 | 0/1 | The current condition on input
| 24 |  | 远程复位安全链信号 | 1 | I16 | 123 | 0/1 | The current condition on output

## 运行
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
25 | Operate | 机组运行状态 | 1 | I16 | 200 | 字符串 | 1:"Starting" 2:"Service" 3:"Yaw into wind" 4:"Selftest run check" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Freewheel init" 12:"Freewheel G1" 13:"Grid connect G1" 14:"Operation G1" 15:"LVRT" 16:"Freewheel G1G1" 17:"Battery test" 18:"Pitch Service Test" 19:"B200" 20:"B199" 21:"B99" 22:"B50" 23:"None"
26 |  | 运行状态剩余时间 | 1000 | I32 | 201-202 | s | Up/down counter estimating the time until the end of this state. When it is zero, the state changes. Shows the lowest of the timers, except in the starting state where the highest one is shown.
27 |  | 计时名称 | 1 | I16 | 203 | 字符串 | 1:"Secs until start" 2:"Force start" 3:"Start wind" 4:"Brake cool" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Gen.rpm OK" 12:"State timeout" 13:"Connect window" 14:"Phase Drop" 15:"Power Recovery" 16:"None"
28 |  | 运行步骤 | 1 | I16 | 204 | 字符串 | 1:"None" 2:"Waiting for MDS" 3:"Waiting for Grid" 4:"STEP 1" 5:"STEP 2" 6:"STEP 3" 7:"STEP 4" 8:"STEP 5"
29 |  | 运行模式 | 1 | I16 | 205 | 字符串 | 1:"RUN-AUTO" 2:"RUN-SERVICE" 3:"SERVICE" 4:"UNKNOWN"
30 |  | 变桨模式 | 1 | I16 | 206 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"ESTOP" 4:"UNKNOWN"
31 |  | 变频器模式 | 1 | I16 | 207 | 字符串 | 1:"RUN" 2:"STOP" 3:"UNKNOWN"
32 |  | 变桨MDS模式 | 1 | I16 | 208 | 字符串 | 1:"SAFETY" 2:"OPERATE" 3:"SERVICE" 4:"BATTERYTEST1" 5:"BATTERYTEST2" 6:"BATTERYTEST3" 7:"TEST" 8:"SIMULATE" 9:"UNKNOWN"
33 |  | 变桨位置极限 | 100 | I32 | 209-210 | ° | Min. allowed pitch angle, sent to Pitch Controller
34 |  | 变桨速度极限 | 100 | I32 | 211-212 | °/s | Max. allowed pitch speed, sent to Pitch Controller
35 |  | 发电机转速极限 | 100 | I32 | 213-214 | rpm | Max. allowed generator rpm, sent to Pitch Controller.
36 |  | 转矩极限 | 10 | I32 | 215-216 | Nm | Max. allowed torque, sent to Torque Controller.
37 |  | 制动冷却时间 | 1000 | I32 | 217-218 | S | Time until brakes have been cooled down after applying. When 0 the turbine can be started. This timer uses value from the parameter Brake Cool xxx s p. 169. The timer can be used as state timer in the operational state Starting (see 2.6.2.2). The timer counts down to 0 if mechanical brake is released (3.3#16 "HYDRAULIC VALVE BRAKER OPEN" p. 658 = 0) or if "Zero rpm" ( Rotor xxxxxxxx.xxx rpm p. 331 < 2 rpm and Generator xxxxxxxx.x rpm p. 306 < 2 rpm * Gear Ratio xxx.xx p. 351) is reached.
386 | Turbine Status | 风机限功状态 | 1 | I16 | 3200 | 0/1
387 |  | 风机发电状态 | 1 | I16 | 3201 | 0/1
388 |  | 风机待机状态 | 1 | I16 | 3202 | 0/1
389 |  | 风机停机状态 | 1 | I16 | 3203 | 0/1
390 |  | 风机维护状态 | 1 | I16 | 3204 | 0/1
391 |  | 机组有功功率设定值（可写） | 1000 | I32 | 3205-3206 | kw
392 |  | 机组无功功率设定值（可写） | 1000 | I32 | 3207-3208 | kVAr
392+ |  | 机组控制(可写) | 1 | I16 | 3209 | - | 1：启动 2：停止 3：复位

## 偏航
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 38 | Yaw | 当前偏航程序 | 1 | I16 | 300 | / | Shows the active yaw program (0,30,50,60, 70, 80, 100, 230 or 240).
| 39 |  | 当前偏航状态 | 1 | I16 | 301 | 字符串 | 1:"STOPPED" 2:"START CW" 3:"STARTCCW" 4:"RUN. CW" 5:"STOPPING" 6:"RUN. CCW" 7:"STOPPING"
| 40 |  | 偏航自动模式 | 1 | I16 | 302 | 0/1
| 41 |  | 顺时针解缆限位开关 | 1 | I16 | 303 | 0/1 | The current condition on input
| 42 |  | 逆时针解缆限位开关 | 1 | I16 | 304 | 0/1 | The current condition on input
1 | 43 |  | 顺时针偏航 | 1 | I16 | 305 | 0/1 | The current condition on output
| 44 |  | 顺时针偏航继电器反馈 | 1 | I16 | 306 | 0/1 | The current condition on input
1 | 45 |  | 逆时针偏航 | 1 | I16 | 307 | 0/1 | The current condition on output
| 46 |  | 逆时针偏航继电器反馈 | 1 | I16 | 308 | 0/1 | The current condition on input
| 47 |  | 偏航系统供电回路反馈 | 1 | I16 | 309 | 0/1 | The current condition on input
| 48 |  | 偏航半压制动 | 1 | I16 | 310 | 0/1 | The current condition on output
| 49 |  | 偏航全压制动 | 1 | I16 | 311 | 0/1 | The current condition on output
| 50 |  | 偏航电磁制动 | 1 | I16 | 312 | 0/1 | The electrical yaw brake
1 | 51 |  | 机舱相对正北角度 | 10 | I16 | 313 | ° | Shows the position of the nacelle in context to a circle were 0°is North.
1 | 52 |  | 机舱相对风向角度 | 10 | I16 | 314 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned correctly according to the wind direction.
1 | 53 |  | 偏航传感器A | 1 | I16 | 315 | 0/1 | The current condition on input
1 | 54 |  | 偏航传感器B | 1 | I16 | 316 | 0/1 | The current condition on input
| 55 |  | 解缆传感器（0=逆时针/1=顺时针） | 1 | I16 | 317 | 0/1 | Shows which way the cable is twisted (1 = Cw / 0 = Ccw).
1 | 56 |  | 解缆角度 | 10 | I32 | 318-319 | ° | Shows how many degrees the cables in the tower are twisted. To reset the value
| 57 |  | 偏航程序模式 | 1 | I16 | 320 | 0/1 | Shows the active yaw program.
1 | 58 |  | 顺时针偏航倒计时 | 1000 | I32 | 321-322 | s | Yaw delay for the CW direction.
1 | 59 |  | 逆时针偏航倒计时 | 1000 | I32 | 323-324 | s | Yaw delay for the CCW direction.

## 变桨
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 67 | Pitch | 功率设定值 | 1000 | I32 | 502-503 | KW | Power setpoint from Operate to the PID controller
1 | 68 |  | 变桨角度 | 100 | I32 | 504-505 | ° | Simple average of the actual 3 pitch angles.
1 | 69 |  | 变桨角度设定值 | 100 | I32 | 506-507 | ° | Angle Setpoint sent to the Blade controller
1 | 70 |  | 变桨速度 | 100 | I32 | 508-509 | °/s | Pitch speed.
| 71 |  | PID输入模式 | 1 | I16 | 510 | 字符串 | 1:"SPEED" 2:"AUTO"
| 72 |  |  | 1 | I16 | 511 | 字符串 | 1:"ENABLED" 2:"DISABLED"
| 73 |  |  | 1 | I16 | 512 | 字符串 | 1:"ENABLED" 2:"DISABLED"
| 75 | Blade Controller | 变桨当前模式 | 1 | I16 | 600 | 字符串 | 1:"Safety" 2:"Operate" 3:"Service" 4:"Batterytest1" 5:"Batterytest2" 6:"Batterytest3" 7:"Test mode" 8:"Simulate Pitch"
| 76 |  | 变桨速度限值 | 100 | I32 | 601-602 | ° | Pitch speed limit from the pitch regulator.
1 | 77 |  | 变桨角度设定值 | 100 | I32 | 603-604 | °
1 | 78 |  | 1号桨叶角度 | 100 | I32 | 605-606 | ° | Actual pitch angle blade 1.
1 | 79 |  | 2号桨叶角度 | 100 | I32 | 607-608 | ° | Actual pitch angle blade 2.
1 | 80 |  | 3号桨叶角度 | 100 | I32 | 609-610 | ° | Actual pitch angle blade 3.
1 | 81 |  | 1号桨叶当前故障 | 1 | I16 | 611 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
1 | 82 |  | 2号桨叶当前故障 | 1 | I16 | 612 | / | Lists active faults on Blade 2. When a unit contains multiple active faults,the value toggles each second to display active faults.
1 | 83 |  | 3号桨叶当前故障 | 1 | I16 | 613 | / | Lists active faults on Blade 3. When a unit contains multiple active faults,the value toggles each second to display active faults.
1 | 84 |  | 1号桨叶当前报警 | 1 | I16 | 614 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
1 | 85 |  | 2号桨叶当前报警 | 1 | I16 | 615 | / | Lists active warnings on Blade 2. When a unit contains multiple active warnings the value toggles each second to display active warnings.
1 | 86 |  | 3号桨叶当前报警 | 1 | I16 | 616 | / | Lists active warnings on Blade 3. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 87 |  | Modbus驱动器控制 | 1 | I16 | 617 | 字符串 | 1:"Run" 2:"Config"
1 | 88 |  | 1号桨叶MDS通讯OK | 1 | I16 | 618 | 0/1 | Indicates communication status towards Blade 1.
1 | 89 |  | 2号桨叶MDS通讯OK | 1 | I16 | 619 | 0/1 | Indicates communication status towards Blade 2.
1 | 90 |  | 3号桨叶MDS通讯OK | 1 | I16 | 620 | 0/1 | Indicates communication status towards Blade 3.
| 91 |  | 复位变桨通讯状态（可写） | 1 | I16 | 621 | 0/1 | This setting must be updated to 1 to reset MDS communication related statistics. After the update the setting will automatically return to 0.
| 92 |  | 通讯信息 | 1 | I16 | 622 | /
| 93 |  | MDS1读取的请求数量 | 1 | I16 | 623 | / | Number of read requests sent.
| 94 |  | MDS1收到的响应数量 | 1 | I16 | 624 | / | Number of received reponses.
| 95 |  | MDS1丢失的响应数量 | 1 | I16 | 625 | / | Number of missing responses.
| 96 |  | CRC故障 | 1 | I16 | 626 | /
| 97 |  | MDS1结构故障数量 | 1 | I16 | 627 | / | Number of responses received containing framing errors.
| 98 |  | MDS2读取的请求数量 | 1 | I16 | 628 | / | Number of read requests sent.
| 99 |  | MDS2收到的响应数量 | 1 | I16 | 629 | / | Number of received reponses.
| 100 |  | MDS2丢失的响应数量 | 1 | I16 | 630 | / | Number of missing responses.
| 101 |  | CRC故障 | 1 | I16 | 631 | /
| 102 |  | MDS2结构故障数量 | 1 | I16 | 632 | / | Number of responses received containing framing errors.
| 103 |  | MDS3读取的请求数量 | 1 | I16 | 633 | / | Number of read requests sent.
| 104 |  | MDS3收到的响应数量 | 1 | I16 | 634 | / | Number of received reponses.
| 105 |  | MDS3丢失的响应数量 | 1 | I16 | 635 | / | Number of missing responses.
| 106 |  | CRC故障 | 1 | I16 | 636 | /
| 107 |  | MDS3结构故障数量 | 1 | I16 | 637 | / | Number of responses received containing framing errors.
| 108 |  | 变桨1软件版本 | 1 | I32 | 638-639 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 109 |  | 变桨1当前模式 | 1 | I16 | 640 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man."
| 110 |  | 变桨1以安全速度切出 | 1 | I16 | 641 | 字符串 | 1:"Normal" 2:"Safety"
| 111 |  | 变桨1当前故障 | 1 | I16 | 642 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
| 112 |  | 变桨1当前报警 | 1 | I16 | 643 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 113 |  | 变桨1电机状态 | 1 | I16 | 644 | 字符串 | 1:"Stopped" "Started"
| 114 |  | 变桨1制动状态 | 1 | I16 | 645 | 字符串 | 1:"Released" 2:"Activated"
| 115 |  | 变桨1电池状态 | 1 | I16 | 646 | 字符串 | 1:"Disconnected" 2:"Connected"
| 116 |  | 变桨1进程状态 | 1 | I16 | 647 | 字符串 | 1:"Disable" 2:"Enable"
| 117 |  | 变桨1轮毂维护使能 | 1 | I16 | 648 | 0/1 | Specifies the hub service state on the MDS unit.
| 118 |  | 变桨2软件版本 | 1 | I32 | 649-650 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 119 |  | 变桨2当前模式 | 1 | I16 | 651 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man."
| 120 |  | 变桨2以安全速度切出 | 1 | I16 | 652 | 字符串 | 1:"Normal" 2:"Safety"
| 121 |  | 变桨2当前故障 | 1 | I16 | 653 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
| 122 |  | 变桨2当前报警 | 1 | I16 | 654 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 123 |  | 变桨2电机状态 | 1 | I16 | 655 | 字符串 | 1:"Stopped" "Started"
| 124 |  | 变桨2制动状态 | 1 | I16 | 656 | 字符串 | 1:"Released" 2:"Activated"
| 125 |  | 变桨2电池状态 | 1 | I16 | 657 | 字符串 | 1:"Disconnected" 2:"Connected"
| 126 |  | 变桨2进程状态 | 1 | I16 | 658 | 字符串 | 1:"Disable" 2:"Enable"
| 127 |  | 变桨2轮毂维护使能 | 1 | I16 | 659 | 0/1 | Specifies the hub service state on the MDS unit.
| 128 |  | 变桨3软件版本 | 1 | I32 | 660-661 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 129 |  | 变桨3当前模式 | 1 | I16 | 662 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man."
| 130 |  | 变桨3以安全速度切出 | 1 | I16 | 663 | 字符串 | 1:"Normal" 2:"Safety"
| 131 |  | 变桨3当前故障 | 1 | I16 | 664 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
| 132 |  | 变桨3当前报警 | 1 | I16 | 665 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 133 |  | 变桨3电机状态 | 1 | I16 | 666 | 字符串 | 1:"Stopped" "Started"
| 134 |  | 变桨3制动状态 | 1 | I16 | 667 | 字符串 | 1:"Released" 2:"Activated"
| 135 |  | 变桨3电池状态 | 1 | I16 | 668 | 字符串 | 1:"Disconnected" 2:"Connected"
| 136 |  | 变桨3进程状态 | 1 | I16 | 669 | 字符串 | 1:"Disable" 2:"Enable"
| 137 |  | 变桨3轮毂维护使能 | 1 | I16 | 670 | 0/1 | Specifies the hub service state on the MDS unit.
| 138 |  | 上一次电池测试2/3时间 | 1 | I64 | 671-674 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 139 |  | 1号桨叶上一次电池测试电压 | 1 | I16 | 675 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 1.
| 140 |  | 2号桨叶上一次电池测试电压 | 1 | I16 | 676 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 2.
| 141 |  | 3号桨叶上一次电池测试电压 | 1 | I16 | 677 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 3.
| 142 |  | 电池测试请求信号 | 1 | I16 | 678 | 0/1 | The MDS system has requested the operation program to perform a battery test 2 or 3.
|  |  | 手动电池测试请求（可写） |  | I16 | 679 | 0/1
| 143 |  | 电池测试故障 | 1 | I16 | 680 | 0/1 | Indicates if the latest battery test failed. A successfull battery test is required before the turbine is allowed to start.

## 转矩
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 144 | Torque | 转矩控制器状态 | 1 | I16 | 700 | 字符串 | 1:"OFF (Limited to 0Nm)" 2:"L PI Grid Connect X.Ys" 3:"L PI Ramp Lower Limit" 4:"L PI Ramp to G1G1" 5:"L PI Active" 6:"Speed Ctrl. Await Torque" 7:"Critical Torque" 8:"Critical Torque" 9:"Power-Speed Red. ZkW" 10:"Power Red. ZkW" 11:"Power Control Rated Power" 12:"Speed Ctrl. Await Op. RPM SP" 13:"Exiting Power Control" 14:"Torque Table Lookup"
1 | 145 |  | 转矩设定值 | 10 | I32 | 701-702 | Nm | Torque Setpoint calculated by the torque controller
1 | 146 |  | 转矩设定百分比 | 100 | I16 | 703 | % | Shows torque setpoint in percents
1 | 147 |  | 发电机转速 | 100 | I32 | 704-705 | rpm
| 148 |  | PI控制器的发电机转速设定值 | 100 | I32 | 706-707 | rpm | Generator speed setpoint for the torque PI controller. See section 2.10.1.2 for details.
| 149 |  | 发电机额定转速设定值 | 100 | I32 | 708-709 | rpm | Operational Speed setpoint. This is the rated speed of the turbine. See Operate object for details.
| 150 |  | 最小转矩限值百分比 | 100 | I32 | 710-711 | rpm | Define the dynamic minimum torque to be applied. See section 2.10.1.2 for details
| 151 |  | 最大转矩限值百分比3 | 100 | I32 | 712-713 | rpm | Define the dynamic maximum torque to be applied. See section 2.10.1.2 for details.
| 152 |  | 转矩基值 | 10 | I32 | 714-715 | Nm | Baseline used for the torque PI controllers. See section 2.10.2 for details.
| 153 |  | 转矩基值百分比 | 100 | I16 | 716 | % | Baseline used for the torque PI controllers. See section 2.10.2 for details
1 | 154 |  | 网侧功率 | 1000 | I32 | 717-718 | kw | Active power measured by the control system and exponential averaged by Power Average Time x.xx s p. 246.
1 | 155 |  | 发电机功率 | 1000 | I32 | 719-720 | kw | Calculated active power on the generator and exponential averaged by Power Average Time x.xx s p. 246.
1 | 156 |  | 机组消耗功率 | 1000 | I32 | 721-722 | kw | Estimate of auxiliaries consumption to be compensated by the torque controller in Power Control Mode. See section 2.10.3 for details.
| 157 |  | 机械效率 | 1000 | I32 | 723-724 | / | Efficiency based on lookup table Mech. Efficiency Table p. 241

## 变频器
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 158 | Inverter | 变频器模式 | 1 | I16 | 800 | 字符串 | 1:"Reset" 2:"Stopped" 3:"Run" 4:"Grid Connected"
1 | 159 |  | 发电机转速（编码器） | 10 | I16 | 801 | rpm | Actual speed of the generator.
1 | 160 |  | 转矩 | 100 | I16 | 802 | % | Actual Generator torque in percentage
| 161 |  | 控制字 | 1 | I16 | 803 | /
1 | 162 |  | ON(bit 0) | 1 | I16 | 804 | 0/1
1 | 163 |  | RUN(bit 3) | 1 | I16 | 805 | 0/1
1 | 164 |  | RESET(bit 7） | 1 | I16 | 806 | 0/1
1 | 165 |  | 有功功率 | 10 | I16 | 807 | kW | Actual power.
1 | 166 |  | 无功功率 | 10 | I16 | 808 | kvar | Actual reactive power.
1 | 167 |  | 直流母线电压 | 10 | I16 | 809 | V | Mains voltage.
1 | 168 |  | 直流母线电流 | 10 | I16 | 810 | A | Line curreunt.
| 169 |  | 变频器PP温度 | 1 | I16 | 811 | °C | PP temperature in degrees centigrade.
| 170 |  | 变频器制动器 | 1 | I16 | 812 | 0/1 | Shows the status of the inverter brealer on 1.4#31 "Inverter Breaker" p. 545 (0 = Error, 1 = OK)
1 | 171 |  | 转矩变化率 | 100 | I16 | 813 | % | Torque setpoint used to control the inverter.
| 172 |  | 相角变化率 | 100 | I16 | 814 | °
| 284 | LVRT | LVRT上一次触发时间 | 1 | I64 | 1400-1403 | / | The time stamp of the last LVRT situation
| 285 |  | LVRT上一次持续时间 | 1 | I32 | 1404-1405 | ms | The duration time of the last LVRT situation

## 发电机
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
1 | 173 | Generator | 发电机转速（主控） | 100 | I32 | 900-901 | rpm | Generator rpm.
1 | 174 |  | 发电机转速1秒平均值 | 100 | I32 | 902-903 | rpm | Shows the 1 sec. averaged rotor speed
| 175 |  | 发电机转速30秒平均值 | 100 | I32 | 904-905 | rpm | Shows the 30 sec. averaged rotor speed
| 176 |  | 发电机转速10分钟平均值 | 100 | I32 | 906-907 | rpm | Shows the 600 sec. averaged rotor speed
| 177 |  | 发电机加热器模式 | 1 | I16 | 908 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 178 |  | 发电机滑环室加热模式 | 1 | I16 | 909 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 179 |  | 发电机风扇电机加热模式 | 1 | I16 | 910 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 180 |  | 发电机冷却模式 | 1 | I16 | 911 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 181 |  | 发电机滑环室冷却模式 | 1 | I16 | 912 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
1 | 182 |  | 发电机频率 | 1000 | I32 | 913-914 | Hz | Shows the generator speed in Hz.
1 | 183 |  | 发电机L1绕组温度 | 10 | I16 | 915 | °C | Shows the (G) stator winding L1 temperature.
1 | 184 |  | 发电机L2绕组温度 | 10 | I16 | 916 | °C | Shows the (G) stator winding L2 temperature.
1 | 185 |  | 发电机L3绕组温度 | 10 | I16 | 917 | °C | Shows the (G) stator winding L3 temperature.
1 | 186 |  | 发电机驱动端轴承温度 | 10 | I16 | 918 | °C | Shows the (G) bearing DE temperature.
1 | 187 |  | 发电机非驱动端轴承温度 | 10 | I16 | 919 | °C | Shows the (G) bearing NDE temperature.
| 188 |  | 发电机加热器状态 | 1 | I16 | 920 | 0/1 | The current condition on output 3.2#14 "Heating Generator" p. 550 (0 = Heating OFF, 1 = Heating ON).
| 189 |  | 发电机滑环室加热器状态 | 1 | I16 | 921 | 0/1
| 190 |  | 发电机风扇加热器状态 | 1 | I16 | 922 | 0/1
| 191 |  | 发电机加热器反馈 | 1 | I16 | 923 | 0/1 | Heating feedback signal 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK).
| 192 |  | 发电机前置风扇反馈 | 1 | I16 | 924 | 0/1 | The current condition on output 3.2#16 "Generator Fan Front" p. 550 (0 = Fan OFF, 1 = Fan ON).
| 193 |  | 发电机顶部风扇反馈 | 1 | I16 | 925 | 0/1 | The current condition on output 3.2#17 "Generator Fan Top" p. 550 (0 = Fan OFF, 1 = Fan ON).
| 194 |  | 发电机滑环室风扇反馈 | 1 | I16 | 926 | 0/1
| 195 |  | 发电机风扇断路器反馈 | 1 | I16 | 927 | 0/1 | The current state of the fan feedback on 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK).
| 196 |  | 发电机碳刷报警 | 1 | I16 | 928 | 0/1 | The current state of the brush wear on 3.3#41 "Generator Brush Wear Error" p. 555 (0 = ERROR, 1 = OK).
1 | 197 |  | 发电机风扇出口温度 | 10 | I16 | 929 | °C | Shows the (G) fan outer temperature.
1 | 198 |  | 发电机滑环室温度 | 10 | I16 | 930 | °C
| 370 | Power Management | 功率控制模式 | 1 | I16 | 2900 | 字符串 | 1:"No Red. Active" 2:"Local, kW" 3:"Local, %" 4:"Remote" 5:"12345678901234567890" 6:"Freq. drop active" 7:"Grid: High Freq." 8:"Low Limit Active"
1 | 371 |  | 有功功率设定值 | 1000 | I32 | 2901-2902 | kW | Shows the requested active power production.
| 372 |  | 有功功率1秒平均值 | 1000 | I32 | 2903-2904 | kW | Active Power 1s xxxxx.x kW
| 373 |  | 有功功率10分钟平均值 | 1000 | I32 | 2905-2906 | kW | 10 minute average value of active power production.
| 374 |  | 无功功率设定值 | 1000 | I32 | 2907-2908 | kvar | Shows the requested reactive power.
| 375 |  | 无功功率1秒平均值 | 1000 | I32 | 2909-2910 | kvar | 1 second average value of reactive power production or consumption.
| 376 |  | 无功功率10分钟平均值 | 1000 | I32 | 2911-2912 | kvar | 10 minute average value of reactive power production or consumption.

## 主轴
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 60 | Brake Disk | 制动模式 | 1 | I16 | 400 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"UNKNOWN"
1 | 61 |  | 制动类型 | 1 | I16 | 401 | 字符串 | 1:"OPEN" 2:"CLOSE" 3:"AUTO CLOSE" 4:"UNKNOWN"
| 62 |  | 制动盘报警 | 1 | I16 | 402 | 0/1 | The current condition on input
| 63 |  | 液压制动松闸（0=抱闸/1=松闸） | 1 | I16 | 403 | 0/1 | The current condition on input
| 64 |  | 主轴制动释放 | 1 | I16 | 404 | 0/1 | 3.2-51#
| 65 |  | 主轴制动抱闸 | 1 | I16 | 405 | 0/1 | 3.2-52#
| 66 |  | 主轴转速设定值 | 100 | I32 | 500-501 | rpm | Speed setpoint from Operate to the PID controller.
1 | 199 | Rotor | 主轴转速 | 100 | I32 | 1000-1001 | rpm | Rotor rpm.
1 | 200 |  | 主轴轴承1温度 | 10 | I16 | 1002 | °C | The current temperature on PT100 input 3.3#69+ "Spindle Bearing 1" p. 620
1 | 201 |  | 主轴轴承2温度 | 10 | I16 | 1003 | °C | The current temperature on PT100 input 3.3#70+ "Spindle Bearing 2" p. 620
1 | 202 |  | 主轴软件超速 | 1 | I16 | 1004 | 0/1 | The current condition on input (0 = OK, 1 = Error).
1 | 203 |  | 液压站过滤器堵塞 | 1 | I16 | 1005 | 0/1 | The current condition on input 3.3#46 "Hydraulic Filter Blocked" p. 555 (1 = Error, 0 = OK). Used in status code 441 - Brake pressure p. 270
1 | 204 |  | 主轴刹车抱闸 | 1 | I16 | 1006 | 0/1 | The current condition on input 3.2#51 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 85 bar.
1 | 205 |  | 主轴刹车释放 | 1 | I16 | 1007 | 0/1 | The current condition on input 3.2#52 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 10 bar.
| 206 |  | 主轴锁定销1释放 | 1 | I16 | 1008 | 0/1 | The current condition on input 3.2#46 "Rotor Unlock 1" p. 551 (1 = Released, 0 = Locked).
| 207 |  | 主轴锁定销2释放 | 1 | I16 | 1009 | 0/1 | The current condition on input 3.2#47 "Rotor Unlock 2" p. 551 (1 = Released, 0 = Locked)
| 208 |  | 滑环加热器断路器反馈 | 1 | I16 | 1010 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK).
1 | 209 |  | 主轴转速1秒平均值 | 100 | I32 | 1011-1012 | rpm | Shows the 1 sec. averaged rotor speed
| 210 |  | 主轴转速30秒平均值 | 100 | I32 | 1013-1014 | rpm | Shows the 30 sec. averaged rotor speed
| 211 |  | 主轴转速10分钟平均值 | 100 | I32 | 1015-1016 | rpm | Shows the 600 sec. averaged rotor speed
1 | 212 |  | 主轴频率 | 1000 | I32 | 1017-1018 | Hz | Shows the rotor frequency from the sensor

## 齿轮箱
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 213 | Gear | 齿轮箱润滑油过滤器压力反馈 | 1 | I16 | 1100 | 0/1 | The current gear oil filter pressure 3.3#43 "Gear Oil Presssure Status" p. 618.
| 214 |  | 齿轮箱过滤器堵塞 | 1 | I16 | 1101 | 0/1 | Filter clogged on 3.3#33 "Gear Box Filter Blooding" p. 618 (1 = clogged, 0 = OK).
| 215 |  | 齿轮箱润滑油油位 | 1 | I16 | 1102 | 0/1 | The current Gear oil level on 3.3#42 "Gear Oil Level/SNK" p. 555 (0=Err, 1=OK).
| 216 |  | 齿轮箱润滑油风扇 | 1 | I16 | 1103 | 0/1 | The current condition on output 3.3#8 "Gear Oil Cooling" p. 554 (0=Off, 1=On).
| 217 |  | 齿轮箱润滑油油泵和风扇断路器反馈 | 1 | I16 | 1104 | 0/1 | The current condition on output 3.3#26 "Feedback MCB Gear Box Oil Pump & Gear Oil Cooler" p. 555 (0=Err, 1=Ok).
| 218 |  | 齿轮箱润滑油加热器 | 1 | I16 | 1105 | 0/1 | The current condition on output 3.2#8 "Gear Oil Heating" p. 550 (0=Off, 1=On).
| 219 |  | 齿轮箱加热器反馈 | 1 | I16 | 1106 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0=Err, 1=Ok).
| 220 |  | 齿轮箱润滑油泵高速 | 1 | I16 | 1107 | 0/1 | The current condition on output 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 (0=Off, 1=On).
| 221 |  | 齿轮箱润滑油泵低速 | 1 | I16 | 1108 | 0/1 | The current condition on output 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 (0=Off, 1=On).
| 222 |  | 齿轮箱风扇电机加热器 | 1 | I16 | 1109 | 0/1 | The current condition on output 3.3#10 "Gear Box Cooler Motor Heater" p. 554 (0=Off, 1=On). This output is set high if 3.3#8 "Gear Oil Cooling" p. 554 is 0.
| 223 |  | 齿轮箱油泵加热器 | 1 | I16 | 1110 | 0/1 | The current condition on output 3.2#19 "Gear Box Pump Heater" p. 551 (0=Off, 1=On). This output is set high if 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 and 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 both are 0.
1 | 224 |  | 齿轮箱油温 | 10 | I16 | 1111 | °C | This parameter shows the actual measured temperature of the gear oil on on 3.3#65+ "Gear Box Oil Temp." p. 556.
1 | 225 |  | 齿轮箱油泵温度 | 10 | I16 | 1112 | °C | The current Gear pump oil temperature on 3.3#66+ "Gear Pump Oil Temp." p. 557.
1 | 226 |  | 齿轮箱轴承1温度 | 10 | I16 | 1113 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557.
1 | 227 |  | 齿轮箱轴承2温度 | 10 | I16 | 1114 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557.
1 | 228 |  | 齿轮箱进口油压 | 100 | I32 | 1115-1116 | bar | The current gear box import oil pressure on 3.2#64+ "Gear Box Import Oil Pressure" p. 552.
1 | 229 |  | 过滤器进口油压 | 100 | I32 | 1117-1118 | bar | The current filter import oil pressure on 3.2#63+ "Filter Import Oil Pressure" p. 552.

## 电网
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
1 | 230 | Grid | 电网电压 | 1 | I32 | 1200-1201 | V | The average of the three measured "Line to neutral"-voltages
1 | 231 |  | 电网电流 | 1 | I16 | 1202 | A | The average current for all three lines.
1 | 232 |  | 电网频率 | 1000 | I32 | 1203-1204 | Hz | The grid frequency measured by the grid module
1 | 233 |  | 电网有功功率 | 1000 | I32 | 1205-1206 | kW | The active power measured by the grid module
1 | 234 |  | 电网无功功率 | 1000 | I32 | 1207-1208 | kVAr | The reactive power measured by the grid module.
| 235 |  | 电网功率因数 | 1000 | I16 | 1209 | / | The power factor calculated by the grid module
1 | 236 |  | 电网L1相电压 | 1 | I32 | 1210-1211 | V | The L1 Voltage "Line to Neutral" measured by the grid module
1 | 237 |  | 电网L2相电压 | 1 | I32 | 1212-1213 | V | The L2 Voltage "Line to Neutral" measured by the grid module.
1 | 238 |  | 电网L3相电压 | 1 | I32 | 1214-1215 | V | The L3 Voltage "Line to Neutral" measured by the grid module.
1 | 239 |  | 电网L1相电流 | 1 | I16 | 1216 | A | The current on L1 measured by the grid module.
1 | 240 |  | 电网L2相电流 | 1 | I16 | 1217 | A | The current on L2 measured by the grid module.
1 | 241 |  | 电网L3相电流 | 1 | I16 | 1218 | A | The current on L3 measured by the grid module.
| 242 |  | 电网L1/L2相位角 | 1000 | I32 | 1219-1220 | ° | The phase angle between L1-L2.
| 243 |  | 电网L1/L3相位角 | 1000 | I32 | 1221-1222 | ° | The phase angle between L1-L3
| 244 |  | 有功功率100毫秒平均值 | 1000 | I32 | 1223-1224 | KW
| 245 |  | 有功功率1秒平均值 | 1000 | I32 | 1225-1226 | KW
| 246 |  | 有功功率3秒平均值 | 1000 | I32 | 1227-1228 | KW
| 247 |  | 有功功率30秒平均值 | 1000 | I32 | 1229-1230 | KW
| 248 |  | 有功功率10分钟平均值 | 1000 | I32 | 1231-1232 | KW
| 249 |  | 无功功率100毫秒平均值 | 1000 | I32 | 1233-1234 | kvar
| 250 |  | 无功功率1秒平均值 | 1000 | I32 | 1235-1236 | kvar
| 251 |  | 无功功率3秒平均值 | 1000 | I32 | 1237-1238 | kvar
| 252 |  | 无功功率30秒平均值 | 1000 | I32 | 1239-1240 | kvar
| 253 |  | 无功功率10分钟平均值 | 1000 | I32 | 1241-1242 | kvar
| 254 |  | L1相电压互感器变比 | 1000 | I32 | 1243-1244 | /
| 255 |  | L2相电压互感器变比 | 1000 | I32 | 1245-1246 | /
| 256 |  | L3相电压互感器变比 | 1000 | I32 | 1247-1248 | /
| 257 |  | L1相电流互感器变比 | 1000 | I32 | 1249-1250 | /
| 258 |  | L2相电流互感器变比 | 1000 | I32 | 1251-1252 | /
| 259 |  | L3相电流互感器变比 | 1000 | I32 | 1253-1254 | /
| 260 |  | 电网L1相峰值电压 | 1 | I32 | 1255-1256 | V | The highest voltage measured on L1 based on "Line to Neutral".
| 261 |  | 电网L1相峰值电压发生时间 | 1 | I64 | 1257-1260 | / | This menuline shows the timestamp for when the voltage peak, see Peak Volt. L1 x V p. 332, occured.
| 262 |  | 电网L2相峰值电压 | 1 | I32 | 1261-1262 | V | The highest voltage measured on L2 based on "Line to Neutral".
| 263 |  | 电网L2相峰值电压发生时间 | 1 | I64 | 1263-1266 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L2 x V p. 332, occured.
| 264 |  | 电网L3相峰值电压 | 1 | I32 | 1267-1268 | V | The highest voltage measured on L3 based on "Line to Neutral".
| 265 |  | 电网L3相峰值电压发生时间 | 1 | I64 | 1269-1272 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L3 x V p. 332, occured.
| 266 |  | 电网L1相峰值电流 | 1 | I32 | 1273-1274 | A | The highest current measured on L1
| 267 |  | 电网L1相峰值电流发生时间 | 1 | I64 | 1275-1278 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L1 x A p. 332, occured.
| 268 |  | 电网L2相峰值电流 | 1 | I32 | 1279-1280 | A | The highest current measured on L2.
| 269 |  | 电网L2相峰值电流发生时间 | 1 | I64 | 1281-1284 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L2 x A p. 333, occured.
| 270 |  | 电网L3相峰值电流 | 1 | I32 | 1285-1286 | A | The highest current measured on L3
| 271 |  | 电网L3相峰值电流发生时间 | 1 | I64 | 1287-1290 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L3 x A p. 333, occured.
| 272 |  | 电网L1相最大正向矢量波动值 | 1000 | I32 | 1291-1292 | ° | The highest positive peak vector surge on L1.
| 273 |  | 电网L1相最大正向矢量波动值发生时间 | 1 | I64 | 1293-1296 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L1 x.x ° p. 333, has occured.
| 274 |  | 电网L2相最大正向矢量波动值 | 1000 | I32 | 1297-1298 | ° | The highest positive peak vector surge on L2.
| 275 |  | 电网L2相最大正向矢量波动值发生时间 | 1 | I64 | 1299-1302 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L2 x.x ° p. 333, has occured.
| 276 |  | 电网L3相最大正向矢量波动值 | 1000 | I32 | 1303-1304 | ° | The highest positive peak vector surge on L3
| 277 |  | 电网L3相最大正向矢量波动值发生时间 | 1 | I64 | 1305-1308 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L3 x.x ° p. 334, has occured
| 278 |  | 电网L1相最大负向矢量波动值 | 1000 | I32 | 1309-1310 | ° | The highest negative peak vector surge on L1
| 279 |  | 电网L1相最大负向矢量波动值发生时间 | 1 | I64 | 1311-1314 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L1 x.x ° p. 334, has occured.
| 280 |  | 电网L2相最大负向矢量波动值 | 1000 | I32 | 1315-1316 | ° | The highest negative peak vector surge on L2
| 281 |  | 电网L2相最大负向矢量波动值发生时间 | 1 | I64 | 1317-1320 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L2 x.x ° p. 334, has occured.
| 282 |  | 电网L3相最大负向矢量波动值 | 1000 | I32 | 1321-1322 | ° | The highest negative peak vector surge on L3.
| 283 |  | 电网L3相最大负向矢量波动值发生时间 | 1 | I64 | 1323-1326 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L3 x.x ° p. 334, has occured.

## 液压站
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 286 | Hydraulic | 液压站状态 | 1 | I16 | 1500 | 字符串 | 1:"Blocked" 2:"Service On" 3:"Service Off" 4:"Auto"
| 287 |  | 液压站油泵状态 | 1 | I16 | 1501 | 0/1 | The current condition on 3.2#7 "Hydraulic pump" p. 550 (0 = Off, 1 = On).
| 288 |  | 液压站油泵过载（0=Error/1=OK） | 1 | I16 | 1502 | 0/1 | The current condition on input 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK).
| 289 |  | 液压站油位 | 1 | I16 | 1503 | 0/1 | The current condition on input 3.3#38 "Hydraulic Oil Level" p. 555 (0 = Low, 1 = OK).
| 290 |  | 液压站温度高（>70） | 1 | I16 | 1504 | 0/1 | The current condition on input 3.3#28 "Hydraulic Temp. High (>=70 °C)" p. 555 (0 = OK, 1 = High).
| 291 |  | 液压站系统压力（1=OK/0=Low） | 1 | I16 | 1505 | 0/1 | The current pressure condition on input 3.3#44 "Hydraulic System Pressure Motor Start (Position 40)" p. 555 (1 = OK, 0 = Low).
| 292 |  | 液压站系统压力（1=OK/0=High） | 1 | I16 | 1506 | 0/1 | The current pressure condition on input 3.3#45 "" p. 555 (1 = OK, 0 = High).
1 | 293 |  | 液压站压力 | 100 | I32 | 1507-1508 | bar | The current condition on the scaled input 3.2#62+ "Hydraulic Pressure" p. 552 (in bar).

## 反馈点error
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
294 | PT100 | 反馈点1.4.65信号错误 | 1 | I16 | 1600 | 0/1
295 |  | 反馈点1.4.66信号错误 | 1 | I16 | 1601 | 0/1
296 |  | 反馈点1.4.67信号错误 | 1 | I16 | 1602 | 0/1
297 |  | 反馈点1.4.68信号错误 | 1 | I16 | 1603 | 0/1
298 |  | 反馈点1.4.69信号错误 | 1 | I16 | 1604 | 0/1
299 |  | 反馈点3.2.65信号错误 | 1 | I16 | 1605 | 0/1
300 |  | 反馈点3.2.66信号错误 | 1 | I16 | 1606 | 0/1
301 |  | 反馈点3.2.67信号错误 | 1 | I16 | 1607 | 0/1
302 |  | 反馈点3.2.68信号错误 | 1 | I16 | 1608 | 0/1
303 |  | 反馈点3.2.69信号错误 | 1 | I16 | 1609 | 0/1
304 |  | 反馈点3.2.70信号错误 | 1 | I16 | 1610 | 0/1
305 |  | 反馈点3.2.71信号错误 | 1 | I16 | 1611 | 0/1
306 |  | 反馈点3.2.72信号错误 | 1 | I16 | 1612 | 0/1
307 |  | 反馈点3.3.65信号错误 | 1 | I16 | 1613 | 0/1
308 |  | 反馈点3.3.66信号错误 | 1 | I16 | 1614 | 0/1
309 |  | 反馈点3.3.67信号错误 | 1 | I16 | 1615 | 0/1
310 |  | 反馈点3.3.68信号错误 | 1 | I16 | 1616 | 0/1
311 |  | 反馈点3.3.69信号错误 | 1 | I16 | 1617 | 0/1
312 |  | 反馈点3.3.70信号错误 | 1 | I16 | 1618 | 0/1
313 |  | 反馈点3.3.72信号错误 | 1 | I16 | 1619 | 0/1
314 | 4-20mA | 反馈点3.2.62信号错误 | 1 | I16 | 1700 | 0/1
315 |  | 反馈点3.2.63信号错误 | 1 | I16 | 1701 | 0/1
316 |  | 反馈点3.3.61信号错误 | 1 | I16 | 1702 | 0/1
317 |  | 反馈点3.3.62信号错误 | 1 | I16 | 1703 | 0/1

## 测风仪
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
318 | Anemometer | 3秒平均风速 | 100 | I16 | 1800 | m/s | This shows the 3 sec. averaged wind speed. | V_WindSpeed3Sec
319 |  | 30秒平均风速 | 100 | I16 | 1801 | m/s | This shows the 30 sec. averaged wind speed | V_WindSpeed30Sec
319+ |  | 10分钟平均风速 | 100 | I16 | 1802 | m/s |  | V_WindSpeed10Min
320 |  | 当前使用的风速仪 | 1 | I16 | 1803 | / | This parameter shows the active anemometer. | V_WindSpeedActive
321 |  | 风速 | 100 | I16 | 1804 | m/s | This parameter shows the wind speed from the selected anemometer. | AI_WindSpeed
322 |  | 风速仪1实际反馈值 | 1000 | I32 | 1805-1806 | Hz |  | HSI_WindSpeedOne_Frq
323 |  | 风速仪2实际反馈值 | 1000 | I32 | 1807-1808 | Hz |  | HSI_WindSpeedTwo_Frq
324 | Wind Vane | 3秒平均风向 | 10 | I16 | 1900 | ° | Shows the 3 seconds averaged wind direction from the selected windvane. | V_WindVaneDirection3Sec
325 |  | 30秒平均风向 | 10 | I16 | 1901 | ° | Shows the 30 seconds averaged wind direction from the selected wind vane | V_WindVaneDirection30Sec
325+ |  | 10分钟平均风速 | 10 | I16 | 1092 | ° |  | V_WindDirection10M
326 |  | 风向 | 10 | I16 | 1903 | ° | Shows the wind direction from the active wind vane. | AI_WindVaneDirection
327 |  | 机舱相对风向偏移量 | 10 | I16 | 1904 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned according to the correct wind direction. | V_RelaWindVaneDirection3Sec
328 |  | 机舱相对正北角度 | 10 | I16 | 1905 | ° | Shows the position of the nacelle seen in proportion to a circle where 0°is North. | V_NacelleDirection
329 |  | 当前使用的风向仪 | 1 | I32 | 1906-1907 | / | Shows which of the two wind vanes is currently active | V_WindVaneActiveVane
330 |  | 风向仪1相对正北角度 | 10 | I16 | 1908 | ° | Shows the wind direction seen in proportion to a circle where 0°is North. | V_WindDirection1
331 |  | 风向仪2相对正北角度 | 10 | I16 | 1909 | ° | Shows the wind direction 2 seen in proportion to a circle where 0°is North. | V_WindDirection2
332 |  | 风向仪1相对机舱角度 | 10 | I16 | 1910 | ° | Shows the wind vane 1 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection1
333 |  | 风向仪2相对机舱角度 | 10 | I16 | 1911 | ° | Shows the wind vane 2 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection2
334 |  | 风向仪1实际反馈值 | 1000 | I16 | 1912 | mA |  | AI_WindDirection1Current
335 |  | 风向仪2实际反馈值 | 1000 | I16 | 1913 | mA |  | AI_WindDirection2Current
Outdoor

## 塔基
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
1 | 337 |  | 环境温度 | 10 | I16 | 2001 | °C | The measured environment temperature on input 1.4#69+ "Enviroment Temperature" p. 547.
| 338 | Lightning | 塔基柜内浪涌保护器 | 1 | I16 | 2100 | 0/1 | The current state of input 1.4#29 "Surge Protection (Tower Base)" p. 545.
| 340 | Transformer | 箱变温度1 | 10 | I16 | 2200 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546).
| 341 |  | 箱变温度2 | 10 | I16 | 2201 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#68+ "Transfomer Temp. 2" p. 547).
| 342 |  | 35KV开关状态（0=OFF/1=ON） | 1 | I16 | 2202 | 0/1 | Shows the status of the 35 kV switch (Terminal 1.4#33 "Measuring open/close of the 35 kV switch" p. 545, 0 = OFF, 1 = ON).
| 343 |  | 690V开关状态（0=OFF/1=ON） | 1 | I16 | 2203 | 0/1 | Shows the status of the 690 volt switch (Terminal 1.4#34 "Measuring open/close of the 0.69 kV switch" p. 545, 0 = OFF, 1 = ON).
| 344 |  | 箱变温度高 | 1 | I16 | 2204 | 0/1
| 345 |  | 箱变油位状态 | 1 | I16 | 2205 | 0/1
1 | 350 | Tower Base | 塔基温度 | 10 | I16 | 2400 | °C | Tower base temperature (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546)
| 351 |  | 塔基烟雾报警 | 1 | I16 | 2401 | 0/1
| 352 | Ups | UPS通讯OK | 1 | I16 | 2500 | 0/1 | Communication status
| 353 |  | UPS剩余时间 | 1 | I32 | 2501-2502 | s | The measured UPS remaining operation time with nominel load. The value is received through the serial connection to the UPS. In case of any communication error, the UPS remaining time is forced to zero.

## 机舱
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 339 |  | 机舱柜内浪涌保护器 | 1 | I16 | 2101 | 0/1 | The current state of input 3.3#50 "Surge Protection Nacelle" p. 555.
| 346 | Air Pressure | 当前大气压力 | 1 | I16 | 2300 | mbar
| 347 |  | 1秒平均气压 | 1 | I16 | 2301 | mbar
| 348 |  | 30秒平均气压 | 1 | I16 | 2302 | mbar
| 349 |  | 10分钟平均气压 | 1 | I16 | 2303 | mbar
1 | 377 | Vibration monitoring | 振动传感器1通道1值 | 1000 | I16 | 3000 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1
1 | 378 |  | 振动传感器1通道2值 | 1000 | I16 | 3001 | G | Shows the vibration level in sensor WP4084 No. 1, channel 2
| 379 |  | 振动传感器1通道1+2值 | 1000 | I16 | 3002 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1 + channel 2
| 380 |  | 振动传感器1通道1状态 | 1 | I16 | 3003 | 0/1 | Shows the status of the WP4084 No. 1, channel 1 (0 = Ok, 1 = Vibration alarm, 2 = Selftest error). See section 2.39.5 for further details on sensor monitoring.
| 381 |  | 振动传感器1通道2状态 | 1 | I16 | 3004 | 0/1 | Shows the status of the sensor selftest (0 = Idle, 1 = Active). See section 2.39.4 for further details on sensor selftest.
| 382 |  | 软件自检类型 | 1 | I16 | 3005 | 0/1 | Shows the selftest failure delay used by the sensor selftest software. (0 = 24 hours, 1 = 24 minutes). See section 2.39.4 for further details on sensor selftest.
| 383 |  | 振动传感器1通讯状态 | 1 | I16 | 3006 | 字符串 | 1:"Disabled" 2:"Error" 3:"Ok"
| 384 | Flight Warning Light | 航空灯供电OK | 1 | I16 | 3100 | 0/1 | The current condition on input 3.3#36 "Supply Obstruction Lights 1 & 2 230V" p. 555 (0 = Error, 1 = Ok).
| 385 |  | 航空灯故障 | 1 | I16 | 3101 | 0/1 | The current condition on input 3.3#37 "Flight Warning Error" p. 555 (1 = Error, 0 = Ok).
1 | 354 | Lubrication | 发电机润滑油泵状态 | 1 | I16 | 2600 | 0/1
1 | 355 |  | 轮毂轴承润滑油油位 | 1 | I16 | 2601 | 0/1 | The current condition on input 3.3#39 "Pitch Bearing Inner Ring Lubrication Grease Level" p. 555 (0 = Empty, 1 = OK).
1 | 356 |  | 轮毂轴承润滑油堵塞 | 1 | I16 | 2602 | 0/1 | The current condition on input 3.3#40 "Pitch Bearing Inner Ring Lubrication Blinding" p. 555 (Pulsing = OK, Not pulsing = Err).
1 | 357 |  | 轮毂润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2603 | 0/1 | The current condition on output 3.2#20 "Lubrication Pump Pitch System (Outer Ring)" p. 551 (0 = OFF, 1 = ON).
1 | 358 |  | 机舱轴承润滑油油位 | 1 | I16 | 2604 | 0/1
1 | 359 |  | 机舱轴承润滑油堵塞 | 1 | I16 | 2605 | 0/1 | The current condition on input 3.2#43 "Yaw Bear Lubrication Blinding" p. 551 (Pulsing = OK, Not pulsing = Err)
1 | 360 |  | 机舱润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2606 | 0/1 | The current condition on output 3.3#9 "Yaw Lubrication Pump 1" p. 554 (0 = OFF, 1 = ON).
1 | 361 | Nacelle | 机舱温度 | 10 | I16 | 2700 | °C | Nacelle temperature on PT100 input 3.2#65+ "Nacelle Temperature" p. 553.
| 362 |  | 机舱风扇状态 | 1 | I16 | 2701 | 0/1 | Nacelle fan ON/OFF (output 3.2#18 "Nacelle Fan 1 & 2" p. 550).
| 363 |  | 机舱风扇断路器反馈 | 1 | I16 | 2702 | 0/1 | Nacelle fan MCB FB ON/OFF (input 3.3#27 "Feedback MCB" p. 555).
| 364 |  | 机舱加热器1+2状态 | 1 | I16 | 2703 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF"
| 365 |  | 机舱加热器3+4状态 | 1 | I16 | 2704 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF"
| 366 |  | 机舱烟雾报警 | 1 | I16 | 2705 | 0/1
1 | 367 | Panels | 机舱柜温度 | 10 | I16 | 2800 | °C | Shows the status of the nacelle control panel temperature (Terminal 3.2#66+ "Nacelle Panel Temperature" p. 553).
1 | 368 |  | 塔基柜温度 | 10 | I16 | 2801 | °C | Shows the temperature of the tower base panel (Terminal 1.4#65+ "Tower Base Panel Temperature" p. 546).
| 369 |  | 以太网开关OK | 1 | I16 | 2802 | 0/1 | Shows the status of the ethernet switch ES100 (Terminal 1.4#32 "Ethernet Switch ES100 OK" p. 545)

## 统计
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
393 | 机组部件运行统计 | 顺时针偏航激活时长 | 10 | I64 | 3300-3303 | 小时 | DO_YawMotorCw
394 |  | 顺时针偏航激活次数 | 1 | I64 | 3304-3307 | 次
395 |  | 逆时针偏航激活时长 | 10 | I64 | 3308-3311 | 小时 | DO_YawMotorCcw
396 |  | 逆时针偏航激活次数 | 1 | I64 | 3312-3315 | 次
397 |  | 偏航电机激活时长 | 10 | I64 | 3316-3319 | 小时 | V_SumYawMotorActive
398 |  | 偏航电机激活次数 | 1 | I64 | 3320-3323 | 次
399 |  | 刹车盘抱闸时长 | 10 | I64 | 3324-3327 | 小时 | V_SumBrakeDisk
400 |  | 刹车盘抱闸次数 | 1 | I64 | 3328-3331 | 次
401 |  | 刹车盘施放时长 | 10 | I64 | 3332-3335 | 小时 | V_SumBrakeFree
402 |  | 刹车盘释放次数 | 1 | I64 | 3336-3339 | 次
403 |  | 发电机加热器工作时长 | 10 | I64 | 3340-3343 | 小时 | DO_GeneratorHeating
404 |  | 发电机加热器工作次数 | 1 | I64 | 3344-3347 | 次
405 |  | 发电机滑环室加热器工作时长 | 10 | I64 | 3348-3351 | 小时 | DO_GeneratorSRHeater
406 |  | 发电机滑环室加热器工作次数 | 1 | I64 | 3352-3355 | 次
407 |  | 发电机风扇电机加热器工作时长 | 10 | I64 | 3356-3359 | 小时 | DO_GeneratorFansHeater
408 |  | 发电机风扇电机加热器工作次数 | 1 | I64 | 3360-3363 | 次
409 |  | 发电机滑环室风扇工作时长 | 10 | I64 | 3364-3367 | 小时 | DO_GeneratorSRFans
410 |  | 发电机滑环室风扇工作次数 | 1 | I64 | 3368-3371 | 次
411 |  | 发电机风扇1工作时长 | 10 | I64 | 3372-3375 | 小时 | DO_GeneratorFanFront
412 |  | 发电机风扇1工作次数 | 1 | I64 | 3376-3379 | 次
413 |  | 发电机风扇2工作时长 | 10 | I64 | 3380-3383 | 小时 | DO_GeneratorFanTop
414 |  | 发电机风扇2工作次数 | 1 | I64 | 3384-3387 | 次
415 |  | 齿轮箱润滑油加热器工作时长 | 10 | I64 | 3388-3391 | 小时 | DO_GearOilHeating
416 |  | 齿轮箱润滑油加热器工作次数 | 1 | I64 | 3392-3395 | 次
417 |  | 齿轮箱风扇工作时长 | 10 | I64 | 3396-3399 | 小时 | DO_GearOilCoolerHighSpeed
418 |  | 齿轮箱风扇工作次数 | 1 | I64 | 3400-3403 | 次
419 |  | 齿轮箱油泵低速工作时长 | 10 | I64 | 3404-3407 | 小时 | DO_GearBoxOilPumpLowSpeed
420 |  | 齿轮箱油泵低速工作次数 | 1 | I64 | 3408-3411 | 次
421 |  | 齿轮箱油泵高速工作时长 | 10 | I64 | 3412-3415 | 小时 | DO_GearBoxOilPumpHighSpeed
422 |  | 齿轮箱油泵高速工作次数 | 1 | I64 | 3416-3419 | 次
423 |  | 液压站油泵工作时长 | 10 | I64 | 3420-3423 | 小时 | DO_HydraulicPump
424 |  | 液压站油泵工作次数 | 1 | I64 | 3424-3427 | 次
425 |  | 测风仪加热器工作时长 | 10 | I64 | 3428-3431 | 小时 | DO_HeatingWindSensor
426 |  | 测风仪加热器工作次数 | 1 | I64 | 3432-3435 | 次
| 电量统计 | 总发电量 | 1 | I64 | 3500-3503 | kWh | S_TotalProduction
|  | 总用电量 | 1 | I64 | 3504-3507 | kWh
|  | 日发电量 | 1 | I64 | 3508-3511 | kWh
|  | 日用电量 | 1 | I64 | 3512-3515 | kWh
|  | 周发电量 | 1 | I64 | 3516-3519 | kWh
|  | 周用电量 | 1 | I64 | 3520-3523 | kWh
|  | 月发电量 | 1 | I64 | 3524-3527 | kWh
|  | 月用电量 | 1 | I64 | 3528-3531 | kWh
|  | 年发电量 | 1 | I64 | 3532-3535 | kWh
|  | 年用电量 | 1 | I64 | 3536-3539 | kWh
| 时间统计 | 总发电时间 | 10 | I64 | 3540-3543 | 小时 | S_TotalOperation
|  | 日发电时间 | 10 | I64 | 3544-3547 | 小时
|  | 周发电时间 | 10 | I64 | 3548-3551 | 小时
|  | 月发电时间 | 10 | I64 | 3552-3555 | 小时
|  | 年发电时间 | 10 | I64 | 3556-3559 | 小时
|  | 总运行时间 | 10 | I64 | 3560-3563 | 小时 | S_Operate
|  | 日运行时间 | 10 | I64 | 3564-3567 | 小时
|  | 周运行时间 | 10 | I64 | 3568-3571 | 小时
|  | 月运行时间 | 10 | I64 | 3572-3575 | 小时
|  | 年运行时间 | 10 | I64 | 3576-3579 | 小时
|  | 总停机时间 | 10 | I64 | 3580-3583 | 小时 | S_OperationStopped
|  | 日停机时间 | 10 | I64 | 3584-3587 | 小时
|  | 周停机时间 | 10 | I64 | 3588-3591 | 小时
|  | 月停机时间 | 10 | I64 | 3592-3595 | 小时
|  | 年停机时间 | 10 | I64 | 3596-3599 | 小时
|  | 总启动风速时间 | 10 | I64 | 3600-3603 | 小时 | S_Startwind
|  | 日启动风速时间 | 10 | I64 | 3604-3607 | 小时
|  | 周启动风速时间 | 10 | I64 | 3608-3611 | 小时
|  | 月启动风速时间 | 10 | I64 | 3612-3615 | 小时
|  | 年启动风速时间 | 10 | I64 | 3616-3619 | 小时
| 风速统计 | 总平均风速 | 10 | I32 | 3620-3621 | m/s | S_WindspeedAvg
|  | 日平均风速 | 10 | I32 | 3622-3623 | m/s
|  | 周平均风速 | 10 | I32 | 3624-3625 | m/s
|  | 月平均风速 | 10 | I32 | 3626-3627 | m/s
|  | 年平均风速 | 10 | I32 | 3628-3629 | m/s
| 可利用率统计 | 总可利用率 | 100 | F32 | 3630-3631 | % | Availability
|  | 日可利用率 | 100 | F32 | 3632-3633 | %
|  | 周可利用率 | 100 | F32 | 3634-3635 | %
|  | 月可利用率 | 100 | F32 | 3636-3637 | %
|  | 年可利用率 | 100 | F32 | 3638-3639 | %

## 日报
日期 |  | 风电场名称-报表名称
风机编号 | 总发电量 (kWh) | 总发电时间 (h) | 日发电量 (kWh) | 日用电量 （kwh) | 日运行时间 (h) | 日故障时间 (h) | 日大于启动风速时间 (h) | 日发电时间 (h) | 日平均风速 (m/s) | 故障代码 | 备注(故障描述)
1# | 3500-3503 | 3540-3543 | 3508-3511 | 3512-3515 | 3564-3567 | 3584-3587 | 3604-3607 | 3544-3547 | 3630-3631 | 手填 | 手填
| I64 | I64 | I64 | I64 | I64 | I64 | I64 | I64 | I64
合计 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 周报
日期 |  | 风电场名称-报表名称
机组编号 | 周平均风速 （m/s） | 周发电量 （kWh） | 周发电时间 （h） | 周可利用率 （%） | 周可利用率修正 （%） | 可利用率修正原因说明
1# | 3636-3637 | 3516-3519 | 3548-3551 | 3654-3655 | 手填 | 手填
| I32 | I64 | I64 | F32
合计 |  | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 月报
日期 |  | 风电场名称-报表名称
机组编号 | 月平均风速 (m/s) | 月平均环境温度 (℃) | 月发电量 (kWh) | 月用电量 (kWh) | 月发电时间 (h) | 月停机时间 (h) | 月等效利用小时数 (h) | 月可利用率 （%） | 年发电量 (kWh) | 总发电量 (kWh) | 总发电时间 (h) | 总运行时间 (h) | 因电网或业主自身原因 |  |  | 因合同中约定机组故障原因
[13 empty] | 停机时间 (h) | 修正可利用率 （%） | 可利用率修正原因 （如有修正必须注明） | 停机时间 (h) | 修正可利用率 （%） | 可利用率修正原因 （如有修正必须注明）
1# | 3626-3627 | 由SCADA计算 | 3524-3527 | 3528-3531 | 3552-3555 | 3592-3595 | 由SCADA计算 | 3636-3637 | 3532-3535 | 3500-3503 | 3540-3543 | 3560-3563 | 手填 | 手填 | 手填 | 手填 | 手填 | 手填
| I32 | I16 | I64 | I64 | I64 | I64 |  | F32 | I64 | I64 | I64 | I64
合计 |  |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 年报
日期 |  |  | 风电场名称-报表名称
机组编号 | 年平均风速 （m/s） | 年平均环境温度 (℃) | 年发电量 （kW） | 年用电量 (kWh) | 年发电时间 （h） | 年停机时间 (h) | 年等效利用小时数 (h) | 年可利用率 （%） | 总发电量 (kWh) | 总发电时间 (h) | 总运行时间 (h)
1# | 3628-3629 | 由SCADA计算 | 3532-3535 | 3536-3539 | 3556-3559 | 3596-3599 | 由SCADA计算 | 3638-3639 | 3500-3503 | 3540-3543 | 3560-3563
| I32 |  | I64 | I64 | I64 | I64 |  | F32 | I64 | I64 | I64
合计 |  |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 性能指标
日期
机组编号 | 风速 （m/s） | 有功功率 （kw） | 无功功率 （kvar） | 发电机L1绕组温度 (°C) | 发电机L2绕组温度 (°C) | 发电机L3绕组温度 (°C) | 发电机驱动端轴承温度 (°C) | 发电机非驱动端轴承温度 (°C) | 发电机风扇出口温度 (°C) | 发电机滑环室温度 (°C) | 主轴转速 （rpm） | 主轴轴承1温度 (°C) | 主轴轴承2温度 (°C) | 齿轮箱油温 (°C) | 齿轮箱油泵温度 (°C) | 齿轮箱轴承1温度 (°C) | 齿轮箱轴承2温度 (°C) | 齿轮箱进口油压 (bar) | 过滤器进口油压 (bar) | 液压站压力 (bar) | 塔基温度 | 环境温度
1# | 1800 | 807 | 808 | 915 | 916 | 917 | 918 | 919 | 929 | 930 | 1000-1001 | 1002 | 1003 | 1111 | 1112 | 1113 | 1114 | 1115-1116 | 1117-1118 | 1507-1508 | 2400 | 2001
| I16 | I16 | I16 | I16 | I16 | I16 | I16 | I16 | I16 | I16 | I32 | I16 | I16 | I16 | I16 | I16 | I16 | I32 | I32 | I32 | I16 | I16
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 故障代码表
机组故障代码表
故障代码 | 故障名称 | 故障名称 | 故障类型 | 故障级别 | 地址 | 报警:B0 | 一般故障停机:B50 | 快速停机:B99 | 紧急停机:B199/B200
0 | System OK | 系统正常 | 主控 | 报警 | 5000
5 | Vibration | 振动故障 | 机舱 | 紧急停机 | 5010
7 | Turbine is serviced | 机组处于维护模式 | 主控 | 报警 | 5020
10 | Safety Chain Open | 安全链断开 | 安全链 | 紧急停机 | 5030
13 | Manual Stop | 手动停机 | 主控 | 一般故障停机 | 5040
23 | Repeating error | 重复故障 | 主控 | 一般故障停机 | 5050
30 | Nacelle Temp. | 机舱温度报警 | 机舱 | 报警 | 5060
31 | Nacelle Temp. Stop | 机舱温度停机 | 机舱 | 一般故障停机 | 5070
32 | High Temp.Cont.Panel | 控制柜温度过高 | 主控 | 一般故障停机 | 5080
33 | Low Temp.Cont.Panel | 控制柜温度过低 | 主控 | 一般故障停机 | 5090
41 | UPS Battery Low | UPS电池电量低 | 主控 | 快速停机 | 5100
45 | Main ctrl.Supply | 主控模块电源电压低 | 主控 | 快速停机 | 5110
55 | Main ctrl.man.reboot | 主控模块手动重启 | 主控 | 一般故障停机 | 5120
92 | Emer.Stop Nacelle | 机舱紧急停机 | 机舱 | 紧急停机 | 5130
100 | Repeated grid error | 重复电网故障 | 电网 | 快速停机 | 5140
103 | Vector surge | 电网电压矢量浪涌 | 电网 | 紧急停机 | 5150
110 | Voltage high | 电压高于等级1 | 电网 | 快速停机 | 5160
111 | Voltage low | 电压低于等级1 | 电网 | 快速停机 | 5170
113 | Trafo overtemp. | 箱变温度1高报警 | 箱变 | 一般故障停机 | 5180
114 | Trafo temp. stop | 箱变温度2高停机 | 箱变 | 一般故障停机 | 5190
115 | Voltage low level 2 | 电压低于等级2 | 电网 | 快速停机 | 5200
116 | Voltage high level 2 | 电压高于等级2 | 电网 | 快速停机 | 5210
120 | Frequency high | 频率过高 | 电网 | 快速停机 | 5220
121 | Frequency low | 频率过低 | 电网 | 快速停机 | 5230
130 | L1-L2-L3 120° | L1-L2-L3相角过大 | 电网 | 快速停机 | 5240
170 | Grid <> Start Cond. | 电网故障无法启动 | 电网 | 一般故障停机 | 5250
173 | Frequency high 2 | 频率过高2 | 电网 | 快速停机 | 5260
174 | Frequency low 2 | 频率过低2 | 电网 | 快速停机 | 5270
200 | Outdoor Temp. Low | 室外温度过低 | 主控 | 报警 | 5280
201 | Outdoor Temp. High | 室外温度过高 | 主控 | 一般故障停机 | 5290
202 | Wind < power | 风速小于功率 | 机舱 | 一般故障停机 | 5300
203 | Wind > power | 风速大于功率 | 机舱 | 一般故障停机 | 5310
205 | Tower resonance time | 塔基共振时间过长 | 主控 | 一般故障停机 | 5320
210 | Anemom. iced over | 测风仪结冰 | 机舱 | 一般故障停机 | 5330
220 | W.Speed Nonidentical | 两风速仪测量值偏差过大 | 机舱 | 一般故障停机 | 5340
221 | W.Direc. Nonidentical | 两风向仪测量值偏差过大 | 机舱 | 一般故障停机 | 5350
226 | Wind gauge defect | 风测量故障 | 机舱 | 一般故障停机 | 5360
230 | Anemometer 1 defect | 风速仪1故障 | 机舱 | 报警 | 5370
231 | Anemometer 2 defect | 风速仪2故障 | 机舱 | 报警 | 5380
233 | Wind < start cond. | 风速小于启动风速 | 机舱 | 报警 | 5390
234 | Wind < yaw cond. | 风速小于偏航风速 | 机舱 | 报警 | 5400
235 | Windvanes Defect | 风向仪故障 | 机舱 | 一般故障停机 | 5410
236 | Outdoor Temp.LowStp | 室外温度过低停机 | 主控 | 一般故障停机 | 5420
237 | Outdoor Temp.Hi. Stp | 室外温度过高停机 | 主控 | 一般故障停机 | 5430
250 | Wind > max | 风速过大 | 机舱 | 一般故障停机 | 5440
251 | Wind > maxmax | 风速太大 | 机舱 | 一般故障停机 | 5450
260 | Windvane 1 Defect | 风向仪1故障 | 机舱 | 报警 | 5460
261 | Windvane 2 Defect | 风向仪2故障 | 机舱 | 报警 | 5470
270 | Windvane Iced Over | 风向仪结冰 | 机舱 | 一般故障停机 | 5480
300 | (G) Tacho Defect | 发电机转速不匹配 | 发电机 | 快速停机 | 5490
302 | (R) Tacho Defect | 主轴转速不匹配 | 主轴 | 快速停机 | 5500
311 | Rotor Overspeed | 主轴转速 | 主轴 | 紧急停机 | 5510
312 | (G) Overspeed | 发电机超速 | 发电机 | 紧急停机 | 5520
319 | WP2035 (G) Over-speed | WP2035发电机超速 | 发电机 | 紧急停机 | 5530
320 | WP2035 (R) Over-speed | WP2035主轴超速 | 主轴 | 紧急停机 | 5540
346 | (G)oversp. operation | 发电机转速超过运行最大值 | 发电机 | 快速停机 | 5550
352 | (G)Oscillation | 发电机转速震荡 | 发电机 | 一般故障停机 | 5560
414 | Brake not released | 刹车未释放 | 机舱 | 一般故障停机 | 5570
415 | Brake pads worn | 刹车盘磨损报警 | 机舱 | 一般故障停机 | 5580
431 | B50 brake time > max | B50等级刹车时间过长 | 主控 | 快速停机 | 5590
433 | B199 brake time >max | B199等级刹车时间过长 | 主控 | 紧急停机 | 5600
439 | Brake valve error | 刹车阀故障 | 液压站 | 一般故障停机 | 5610
441 | Brake pressure | 刹车压力故障 | 液压站 | 报警 | 5620
500 | (G) Heat Error Repeat | 发电机过热故障重复 | 发电机 | 一般故障停机 | 5630
530 | (G) Power Too High | 发电机功率过高 | 发电机 | 一般故障停机 | 5640
531 | (G) L1 Temp. | 发电机L1绕组温度报警 | 发电机 | 报警 | 5650
532 | (G) L1 Temp. Stop | 发电机L1绕组温度停机 | 发电机 | 一般故障停机 | 5660
533 | (G) L2 Temp. | 发电机L2绕组温度报警 | 发电机 | 一般故障停机 | 5670
534 | (G) L2 Temp. Stop | 发电机L2绕组温度停机 | 发电机 | 一般故障停机 | 5680
535 | (G) L3 Temp. | 发电机L3绕组温度报警 | 发电机 | 一般故障停机 | 5690
536 | (G) L3 Temp. Stop | 发电机L3绕组温度停机 | 发电机 | 一般故障停机 | 5700
549 | (G) Heating FB | 发电机加热器反馈故障 | 发电机 | 一般故障停机 | 5710
554 | (G) Brushes worn | 发电机碳刷报警 | 发电机 | 一般故障停机 | 5720
601 | Current asymmetry | 电网电流不对称 | 电网 | 紧急停机 | 5730
639 | Trafo oil level | 箱变油位低 | 箱变 | 一般故障停机 | 5740
664 | Trafo temp.warning | 箱变温度高报警 | 箱变 | 一般故障停机 | 5750
670 | Lightningprot. tower | 塔基防雷模块故障 | 主控 | 报警 | 5760
671 | Lightningprot.nacel. | 机舱防雷模块故障 | 主控 | 报警 | 5770
700 | Error by yawing | 偏航报警 | 偏航 | 一般故障停机 | 5780
701 | Rep. error by yawing | 偏航报警重复故障 | 偏航 | 一般故障停机 | 5790
706 | Yaw CCW feedback | 偏航逆时针反馈故障 | 偏航 | 一般故障停机 | 5800
707 | Yaw CW feedback | 偏航顺时针反馈故障 | 偏航 | 一般故障停机 | 5810
708 | Twisted CCW | 逆时针解缆 | 偏航 | 一般故障停机 | 5820
709 | Twisted CW | 顺时针解缆 | 偏航 | 一般故障停机 | 5830
715 | Cable autounwind | 自动解缆 | 偏航 | 一般故障停机 | 5840
730 | Yaw sensor defect | 偏航传感器不匹配 | 偏航 | 一般故障停机 | 5850
732 | Manual yaw active | 手动偏航激活 | 偏航 | 报警 | 5860
734 | Nacel.pos<>windvane | 机舱位置与风向偏差过大 | 偏航 | 一般故障停机 | 5870
742 | Yaw sensor A/B | 偏航A/B传感器故障 | 偏航 | 一般故障停机 | 5880
755 | Service yaw | 偏航服务模式 | 偏航 | 一般故障停机 | 5890
760 | Yaw misalignment | 偏航角度误差 | 偏航 | 一般故障停机 | 5900
763 | Yaw sens/drive def. | 偏航驱动故障 | 偏航 | 一般故障停机 | 5910
779 | Auto Calibrate Twist | 自动校准解缆 | 偏航 | 一般故障停机 | 5920
934 | (G) Fan FB | 发电机风扇反馈故障 | 发电机 | 一般故障停机 | 5930
1012 | Inverter Com. Error | 变频器通讯故障 | 变频器 | 紧急停机 | 5940
1023 | Inverter CANopen |  | 变频器 | 紧急停机 | 5950
1040 | CANopen Plc com |  | 变频器 | 紧急停机 | 5960
1041 | CANopen plc can com |  | 变频器 | 紧急停机 | 5970
1045 | CANopen plc EMCY |  | 变频器 | 紧急停机 | 5980
1047 | CANopen inv. rec. |  | 变频器 | 紧急停机 | 5990
1048 | CANopen inv. Send |  | 变频器 | 紧急停机 | 6000
1112 | Selftest timeout | 自检超时 | 主控 | 报警 | 6010
1113 | Pitch angle diff. | 变桨角度不同步 | 变桨 | 一般故障停机 | 6020
1119 | Pitch pos.<>setpoint | 变桨角度与给定值不同步 | 变桨 | 一般故障停机 | 6030
1157 | Pitch ctrl.communic. | 变桨控制通讯 | 变桨 | 紧急停机 | 6040
1181 | Batt.voltage 1 warn. | 1号变桨电池电压报警 | 变桨 | 一般故障停机 | 6050
1182 | Batt.voltage 1 stop | 1号变桨电池电压停机 | 变桨 | 紧急停机 | 6060
1183 | Batt.voltage 2 warn. | 2号变桨电池电压报警 | 变桨 | 一般故障停机 | 6070
1184 | Batt.voltage 2 stop | 2号变桨电池电压停机 | 变桨 | 紧急停机 | 6080
1185 | Batt.voltage 3 warn. | 3号变桨电池电压报警 | 变桨 | 一般故障停机 | 6090
1186 | Batt.voltage 3 stop | 3号变桨电池电压停机 | 变桨 | 紧急停机 | 6100
1187 | Battery test | 变桨电池测试 | 变桨 | 报警 | 6110
1201 | (H) Oil Level Low | 液压站油位低 | 液压站 | 一般故障停机 | 6120
1213 | (H) Oper.Time > Max. | 液压站工作时间过长 | 液压站 | 一般故障停机 | 6130
1223 | (H) sys. press. high | 液压站系统压力高 | 液压站 | 报警 | 6140
1224 | (H) sys. press. low | 液压站系统压力低 | 液压站 | 报警 | 6150
1230 | (H) oil very hot | 液压站油温过热 | 液压站 | 一般故障停机 | 6160
1232 | Oil filter clogged | 齿轮箱过滤去堵塞 | 齿轮箱 | 报警 | 6170
1274 | (H)(P) Overload | 液压站过载 | 齿轮箱 | 一般故障停机 | 6180
1301 | Gear oil filt.defect | 齿轮箱过滤去故障 | 齿轮箱 | 报警 | 6190
1302 | Feedback Gear Cooler | 齿轮箱冷却风扇反馈故障 | 齿轮箱 | 一般故障停机 | 6200
1305 | Gear Oil Low | 齿轮箱油位低 | 齿轮箱 | 一般故障停机 | 6210
1309 | Gear Oil (P) FB | 齿轮箱油泵反馈故障 | 齿轮箱 | 一般故障停机 | 6220
1323 | Gear bearing temp. 1 | 齿轮箱轴承1温度报警 | 齿轮箱 | 报警 | 6230
1324 | Gear Bear.Temp.1Stop | 齿轮箱轴承1温度停机 | 齿轮箱 | 一般故障停机 | 6240
1325 | Gear bearing temp. 2 | 齿轮箱轴承2温度报警 | 齿轮箱 | 报警 | 6250
1326 | Gear Bear.Temp.2Stop | 齿轮箱轴承2温度停机 | 齿轮箱 | 一般故障停机 | 6260
1327 | Gear Oil Hot | 齿轮箱油温过热 | 齿轮箱 | 报警 | 6270
1328 | Gear Oil Temp. Low | 齿轮箱油温低 | 齿轮箱 | 一般故障停机 | 6280
1338 | Gear oil press.error | 齿轮箱油压故障 | 齿轮箱 | 一般故障停机 | 6290
1346 | Gear oil temp. Stop | 齿轮箱油温停机 | 齿轮箱 | 一般故障停机 | 6300
1359 | M.bear 1 temp Max-Max | 主轴轴承1温度过高 | 主轴 | 一般故障停机 | 6310
1360 | M.bear 1 temp Max | 主轴轴承1温度高 | 主轴 | 报警 | 6320
1363 | M.bear 2 temp Max-Max | 主轴轴承2温度过高 | 主轴 | 一般故障停机 | 6330
1364 | M.bear 2 temp Max | 主轴轴承2温度高 | 主轴 | 报警 | 6340
1383 | Gear Heating Failure | 齿轮箱加热器故障 | 齿轮箱 | 一般故障停机 | 6350
1409 | Freq.conv. error | 变频器故障 | 变频器 | 报警 | 6360
1413 | Freq.cnv. tripped | 变频器跳闸 | 变频器 | 快速停机 | 6370
1511 | WP4084 chan. 1 def. | WP4084通道1故障 | 机舱 | 一般故障停机 | 6380
1512 | WP4084 chan. 2 def. | WP4084通道2故障 | 机舱 | 一般故障停机 | 6390
1513 | WP4084 comm. error | WP4084通讯故障 | 机舱 | 一般故障停机 | 6400
1539 | WP4084No1 CH1 level 1 | 1号WP4084通道1超限1 | 机舱 | 一般故障停机 | 6410
1544 | PT100 Defective | PT100故障 | 主控 | 一般故障停机 | 6420
1555 | WP4084No1 CH2 level 1 | 1号WP4084通道2超限1 | 主控 | 一般故障停机 | 6430
1556 | WP4084No1 CH1 level 2 | 1号WP4084通道1超限2 | 主控 | 一般故障停机 | 6440
1557 | WP4084No1 CH2 level 2 | 2号WP4084通道2超限2 | 主控 | 一般故障停机 | 6450
1558 | WP4084No2 CH1 level 1 | 2号WP4084通道1超限1 | 主控 | 一般故障停机 | 6460
1559 | WP4084No2 CH2 level 1 | 2号WP4084通道2超限1 | 主控 | 一般故障停机 | 6470
1561 | Flight warn.ligh.out | 航空灯供电故障 | 机舱 | 报警 | 6480
1564 | WP4084No2 CH1 level 2 | 2号WP4084通道1超限2 | 主控 | 一般故障停机 | 6490
1565 | WP4084No2 CH2 level 2 | 2号WP4084通道2超限2 | 主控 | 一般故障停机 | 6500
1569 | Flight warn.ligh.def | 航空灯故障 | 机舱 | 报警 | 6510
1585 | Rotor Locked | 主轴锁定 | 主轴 | 一般故障停机 | 6520
1595 | Selftest | 自检 | 主控 | 报警 | 6530
1672 | F.conv. MCCB open | 变频器主断路器断开 | 变频器 | 快速停机 | 6540
1684 | F.conv. trans. grid | 变频器未并网 | 变频器 | 快速停机 | 6550
1689 | Timeout grid connect | 电网连接超时 | 变频器 | 快速停机 | 6560
1692 | Tower base temp.warn | 塔基温度报警 | 主控 | 报警 | 6570
1703 | External Stop | 外部停机 | 主控 | 紧急停机 | 6580
1715 | 4-20 mA Signal Stop | 4-20mA信号停机 | 主控 | 一般故障停机 | 6590
1733 | High frq. vib.No1 CH1 | 1号WP4084通道1高频振动报警 | 主控 | 报警 | 6600
1734 | High frq. vib.No1 CH2 | 1号WP4084通道2高频振动报警 | 主控 | 报警 | 6610
1748 | High frq. vib.No2 CH1 | 2号WP4084通道1高频振动报警 | 主控 | 报警 | 6620
1749 | High frq. vib.No2 CH2 | 1号WP4084通道2高频振动报警 | 主控 | 报警 | 6630
1769 | Main ctrl.m.shutdown | 主控模块手动关机 | 主控 | 一般故障停机 | 6640
1832 | B99 brake time > max | B99等级刹车时间过长 | 主控 | 紧急停机 | 6650
1835 | Brake failure | 刹车故障 | 液压站 | 一般故障停机 | 6660
1900 | Pitch inv. 1 error | 1号变桨变频器故障 | 变桨 | 紧急停机 | 6670
1901 | Pitch inv. 2 error | 2号变桨变频器故障 | 变桨 | 紧急停机 | 6680
1902 | Pitch inv. 3 error | 3号变桨变频器故障 | 变桨 | 紧急停机 | 6690
1903 | Battery charger err. | 变桨电池充电器故障 | 变桨 | 一般故障停机 | 6700
1934 | Pitch Lubr. Empty | 变桨润滑油空 | 变桨 | 一般故障停机 | 6710
1942 | Service active hub | 轮毂服务模式 | 变桨 | 报警 | 6720
1975 | Pitch 1 not ready | 1号变桨为准备好 | 变桨 | 紧急停机 | 6730
1976 | Pitch 2 not ready | 2号变桨为准备好 | 变桨 | 紧急停机 | 6740
1977 | Pitch 3 not ready | 3号变桨为准备好 | 变桨 | 紧急停机 | 6750
1995 | Pitch inv. 1 warn. | 1号变桨变频器报警 | 变桨 | 一般故障停机 | 6760
1996 | Pitch inv. 2 warn. | 2号变桨变频器报警 | 变桨 | 一般故障停机 | 6770
1997 | Pitch inv. 3 warn. | 3号变桨变频器报警 | 变桨 | 一般故障停机 | 6780
2035 | (G) Bear.DE Temp | 发电机轴承驱动端温度报警 | 发电机 | 报警 | 6790
2036 | (G) Bear.DE Temp.Stop | 发电机轴承驱动端温度停机 | 发电机 | 一般故障停机 | 6800
2037 | (G) Bear.NDE Temp | 发电机轴承非驱动端温度报警 | 发电机 | 报警 | 6810
2038 | (G) Bear.NDE Tmp.Stp | 发电机轴承非驱动端温度停机 | 发电机 | 一般故障停机 | 6820
2048 | (G) L1 Temp. Min. | 发电机L1相绕组温度过低 | 发电机 | 报警 | 6830
2049 | (G) L2 Temp. Min. | 发电机L2相绕组温度过低 | 发电机 | 报警 | 6840
2050 | (G) L3 Temp. Min. | 发电机L3相绕组温度过低 | 发电机 | 报警 | 6850
2136 | Emer.Stop Tower Base | 塔基紧急停机 | 主控 | 紧急停机 | 6860
2225 | UPS Comm. Lost | UPS通讯丢失 | 主控 | 一般故障停机 | 6870
2267 | Main bear.lubr.empty | 主轴承润滑油空 | 主轴 | 一般故障停机 | 6880
2269 | WP4086No1 acc. Alarm |  | 主控 | 报警 | 6890
2270 | WP4086No1 acc. warn. |  | 主控 | 报警 | 6900
2273 | WP4086No1 lev.1 alarm |  | 主控 | 报警 | 6910
2274 | WP4086No1 lev.1 warn. |  | 主控 | 报警 | 6920
2275 | WP4086No1 lev.2 alarm |  | 主控 | 报警 | 6930
2276 | WP4086No1 lev.2 warn. |  | 主控 | 报警 | 6940
2277 | WP4086No1 lev.3 alarm |  | 主控 | 报警 | 6950
2278 | WP4086No1 lev.3 warn. |  | 主控 | 报警 | 6960
2279 | WP4086 Comm. Error | WP4086通讯故障 | 主控 | 报警 | 6970
2290 | WP4086No1 log ready. | 1号WP4086日志已完成 | 主控 | 报警 | 6980
2291 | WP4086No1 Intern err. | 1号WP4086内部故障 | 主控 | 报警 | 6990
2310 | Gear oil therm. hot | 齿轮箱油泵油温高 | 齿轮箱 | 报警 | 7000
2316 | Gear oil2 press. Low | 齿轮箱进口油压低 | 齿轮箱 | 报警 | 7010
2317 | Gear oil therm. Low | 齿轮箱油泵油温低 | 齿轮箱 | 一般故障停机 | 7020
2403 | Anemometers defect | 风速仪故障 | 机舱 | 一般故障停机 | 7030
2411 | Selftest gridfault | 自检电网故障 | 电网 | 报警 | 7040
2412 | Airstream fan 1 Ovl. | 轴流风扇1过载 | 机舱 | 一般故障停机 | 7050
2419 | Vane Diff. and Ice | 风向仪偏差过大并且结冰 | 机舱 | 一般故障停机 | 7060
2424 | Ice and No Wind Dir. | 风向仪无数值并且结冰 | 机舱 | 一般故障停机 | 7070
2429 | Slip Ring Temp | 发电机滑环室温度报警 | 发电机 | 报警 | 7080
2430 | Emer.Stop Relay | 急停继电器跳闸 | 安全链 | 紧急停机 | 7090
2434 | Safety Chain MCCB | 安全链主回路断开 | 安全链 | 紧急停机 | 7100
2435 | Safety Chain Relay 1 | 安全链继电器1断开 | 安全链 | 紧急停机 | 7110
2436 | Safety Chain Relay 2 | 安全链继电器2断开 | 安全链 | 紧急停机 | 7120
2437 | Continous Reset | 连续复位故障 | 主控 | 快速停机 | 7130
2440 | Manual Safety Stop | 手动安全停机 | 主控 | 紧急停机 | 7140
2444 | Tower base temp.stop | 塔基温度停机 | 主控 | 一般故障停机 | 7150
2451 | Eth.net Switch | 以太网交换机故障 | 主控 | 报警 | 7160
2452 | Smoke nacelle | 机舱烟雾报警 | 主控 | 一般故障停机 | 7170
2475 | Fuse Slipring Heaters | 加热器熔丝反馈故障 | 主控 | 一般故障停机 | 7180
2476 | App. not configured | 应用程序未设置 | 主控 | 报警 | 7190
2607 | Pitch sw. ver. err. | 变桨软件版本错误 | 变桨 | 紧急停机 | 7200
2611 | Pitch param. changed | 变桨系统参数被更改 | 变桨 | 报警 | 7210
2612 | Request Timeout | 请求超时 | 变桨 | 紧急停机 | 7220
2654 | Emergency Pitching | 紧急变桨 | 变桨 | 紧急停机 | 7230
2806 | FRT Power Reduction | 高频降功率 | 主控 | 报警 | 7240
2814 | LVRT active | 低电压穿越激活 | 主控 | 报警 | 7250
2815 | LVRT ended | 低电压穿越结束 | 主控 | 一般故障停机 | 7260
2816 | FRT freq.<unstable |  | 主控 | 报警 | 7270
2817 | FRT freq.>unstable |  | 主控 | 报警 | 7280
2818 | FRT freq.stop | 电网频率震荡超限 | 主控 | 一般故障停机 | 7290
2819 | FRT voltage<unstable |  | 主控 | 报警 | 7300
2820 | FRT voltage>unstable |  | 主控 | 报警 | 7310
2821 | FRT voltage stop | 电网电压震荡超限 | 主控 | 一般故障停机 | 7320
2921 | INV LVRT | 塔基变频器低电压穿越启动 | 变频器 | 报警 | 7330
2934 | Torque control | 转矩给定值变化过高报警 | 主控 | 报警 | 7340
3007 | Slip Ring Temp | 发电机滑环室温度停机 | 发电机 | 一般故障停机 | 7350
5000 | 35 kV switch off | 箱变35KV空开跳闸 | 箱变 | 报警 | 7360
5001 | 690 V switch off | 箱变690V空开跳闸 | 箱变 | 报警 | 7370
5003 | Gear oil2 press.stop | 齿轮箱进口油压停机 | 齿轮箱 | 一般故障停机 | 7380
5004 | Gear oil therm. stop | 齿轮箱油泵温度停机 | 齿轮箱 | 一般故障停机 | 7390
5005 | Pitch Bear. In Blind | 变桨轴承进口堵塞 | 变桨 | 报警 | 7400
5006 | Yaw Bear.Lubr. Blind | 偏航轴承润滑油堵塞 | 偏航 | 报警 | 7410
5009 | (G) Fan Outer temp | 发电机风扇出口温度报警 | 发电机 | 报警 | 7420
5010 | (G) Fan Outer temp | 发电机风扇出口温度停机 | 发电机 | 一般故障停机 | 7430
8404 | Selftest no. 1 | 自检1失败 | 主控 | 快速停机 | 7440
8405 | Selftest no. 2 | 自检2失败 | 主控 | 快速停机 | 7450
8406 | Selftest no. 3 | 自检3失败 | 主控 | 快速停机 | 7460
8407 | Selftest no. 4 | 自检4失败 | 主控 | 快速停机 | 7470
8408 | Selftest no. 5 | 自检5失败 | 主控 | 快速停机 | 7480
8704 | Smoke detector | 烟雾报警 | 主控 | 一般故障停机 | 7490
40170 | 1.1 Failed | 模块1.1失败 | 主控 | 紧急停机 | 7500
40171 | 1.1 Status Error | 模块1.1状态故障 | 主控 | 一般故障停机 | 7510
40172 | 1.1 Temperature Error | 模块1.1温度故障 | 主控 | 一般故障停机 | 7520
40173 | 1.1 Uptime Error | 模块1.1运行时间故障 | 主控 | 报警 | 7530
40174 | 1.1 Virtual Module | 模块1.1虚拟状态 | 主控 | 报警 | 7540
40180 | 1.2 Failed | 模块1.2失败 | 主控 | 紧急停机 | 7550
40181 | 1.2 Status Error | 模块1.2状态故障 | 主控 | 一般故障停机 | 7560
40182 | 1.2 Temperature Error | 模块1.2温度故障 | 主控 | 一般故障停机 | 7570
40183 | 1.2 Uptime Error | 模块1.2运行时间故障 | 主控 | 报警 | 7580
40184 | 1.2 Virtual Module | 模块1.2虚拟状态 | 主控 | 报警 | 7590
40190 | 1.3 Failed | 模块1.3失败 | 主控 | 紧急停机 | 7600
40191 | 1.3 Status Error | 模块1.3状态故障 | 主控 | 一般故障停机 | 7610
40192 | 1.3 Temperature Error | 模块1.3温度故障 | 主控 | 一般故障停机 | 7620
40193 | 1.3 Uptime Error | 模块1.3运行时间故障 | 主控 | 报警 | 7630
40194 | 1.3 Virtual Module | 模块1.3虚拟状态 | 主控 | 报警 | 7640
40200 | 1.4 Failed | 模块1.4失败 | 主控 | 紧急停机 | 7650
40201 | 1.4 Status Error | 模块1.4状态故障 | 主控 | 一般故障停机 | 7660
40202 | 1.4 Temperature Error | 模块1.4温度故障 | 主控 | 一般故障停机 | 7670
40203 | 1.4 Uptime Error | 模块1.4运行时间故障 | 主控 | 报警 | 7680
40204 | 1.4 Virtual Module | 模块1.4虚拟状态 | 主控 | 报警 | 7690
40330 | 2.1 Failed | 模块2.1失败 | 主控 | 紧急停机 | 7700
40331 | 2.1 Status Error | 模块2.1状态故障 | 主控 | 一般故障停机 | 7710
40332 | 2.1 Temperature Error | 模块2.1温度故障 | 主控 | 一般故障停机 | 7720
40333 | 2.1 Uptime Error | 模块2.1运行时间故障 | 主控 | 报警 | 7730
40334 | 2.1 Virtual Module | 模块2.1虚拟状态 | 主控 | 报警 | 7740
40490 | 3.1 Failed | 模块3.1失败 | 主控 | 紧急停机 | 7750
40491 | 3.1 Status Error | 模块3.1状态故障 | 主控 | 一般故障停机 | 7760
40492 | 3.1 Temperature Error | 模块3.1温度故障 | 主控 | 一般故障停机 | 7770
40493 | 3.1 Uptime Error | 模块3.1运行时间故障 | 主控 | 报警 | 7780
40494 | 3.1 Virtual Module | 模块3.1虚拟状态 | 主控 | 报警 | 7790
40500 | 3.2 Failed | 模块3.2失败 | 主控 | 紧急停机 | 7800
40501 | 3.2 Status Error | 模块3.2状态故障 | 主控 | 一般故障停机 | 7810
40502 | 3.2 Temperature Error | 模块3.2温度故障 | 主控 | 一般故障停机 | 7820
40503 | 3.2 Uptime Error | 模块3.2运行时间故障 | 主控 | 报警 | 7830
40504 | 3.2 Virtual Module | 模块3.2虚拟状态 | 主控 | 报警 | 7840
40510 | 3.3 Failed | 模块3.3失败 | 主控 | 紧急停机 | 7850
40511 | 3.3 Status Error | 模块3.3状态故障 | 主控 | 一般故障停机 | 7860
40512 | 3.3 Temperature Error | 模块3.3温度故障 | 主控 | 一般故障停机 | 7870
40513 | 3.3 Uptime Error | 模块3.3运行时间故障 | 主控 | 报警 | 7880
40514 | 3.3 Virtual Module | 模块3.3虚拟状态 | 主控 | 报警 | 7890
64000 | WP4000 Overtemp | WP4000 超温 | 主控 | 一般故障停机 | 7900
64001 | Main power low | 主控功率过低 | 主控 | 紧急停机 | 7910
64002 | Backup power low | 备份功率过低 | 主控 | 紧急停机 | 7920
64003 | File system error | 文件系统故障 | 主控 | 一般故障停机 | 7930
64010 | OS Startup | 操作系统启动 | 主控 | 报警 | 7940
64011 | Manual reboot | 手动重启 | 主控 | 紧急停机 | 7950
64012 | Power fail shutdown | 功率不足关机 | 主控 | 紧急停机 | 7960
64013 | SW Watchdog shutdown | 软件看门狗关机 | 主控 | 紧急停机 | 7970
64014 | CPU Watchdog shutdown | 处理器看门狗关机 | 主控 | 紧急停机 | 7980
64015 | Power On/HW Reset/HW WD | Power On/HW Reset/HW WD | 主控 | 紧急停机 | 7990
64016 | Unknown shutdown | 未知原因关机 | 主控 | 紧急停机 | 8000
64017 | Manual Shutdown | 手动关机 | 主控 | 紧急停机 | 8010
64018 | OS Shutdown | 操作系统关机 | 主控 | 紧急停机 | 8020
64019 | Application not loaded | 应用程序未载入 | 主控 | 紧急停机 | 8030
64020 | Guard_Output_12_SC_Missing | Guard_Output_12_SC_Missing | 主控 | 报警 | 8040
64021 | Guard_Rl1_Allways_ON | Guard_Rl1_Allways_ON | 主控 | 报警 | 8050
64022 | Guard_Rl1_Allways_OFF | Guard_Rl1_Allways_OFF | 主控 | 报警 | 8060
64023 | Guard_Rl2_Allways_ON | Guard_Rl2_Allways_ON | 主控 | 报警 | 8070
64024 | Guard_Rl2_Allways_OFF | Guard_Rl2_Allways_OFF | 主控 | 报警 | 8080
64025 | Guard_Input_10_SC_Missing | Guard_Input_10_SC_Missing | 主控 | 报警 | 8090
64026 | WPLine Init Failed | 模块初始化故障 | 主控 | 报警 | 8100
64027 | WPLine Conf Failed | 模块设置故障 | 主控 | 报警 | 8110
64028 | WPLine Conf Modified | 模块设置更改 | 主控 | 报警 | 8120
64029 | System Warning | 系统报警 | 主控 | 报警 | 8130
64030 | System Error | 系统故障 | 主控 | 一般故障停机 | 8140
64031 | New Software | 新软件 | 主控 | 报警 | 8150
64032 | Request Restart | 请求重启 | 主控 | 报警 | 8160
64033 | Application request reboot | 应用程序请求重启 | 主控 | 报警 | 8170
64035 | IO Warning | IO报警 | 主控 | 报警 | 8180
64036 | Watchdog Timeout | 看门狗超时 | 主控 | 紧急停机 | 8190
64037 | Incomplete shutdown | 不完全关机 | 主控 | 一般故障停机 | 8200
64038 | System repeating error | 系统重复故障 | 主控 | 一般故障停机 | 8210
5002 | Stop by PPM | PPM停机 | 主控 | 一般故障停机 | 8220
5007 | PPMAPComError | PPM有功通讯中断 | 主控 | 报警 | 8230
5008 | PPMRPComError | PPM无功通讯中断 | 主控 | 报警 | 8240
5011 | RPowerSpTooHigh | PPM给定无功过高 | 主控 | 报警 | 8250