## 2MW机型总点表
序号 | 目录 |  | 名称 | Config |  |  | 单位 | 描述 | 变量名
|  |  |  | 倍数 | 数据类型 | 地址
1 | Turbine to PPM | 有功 | 有功握手信号 | 1 | I16 | 4000 | - |  | V_SentToPPMAPCount
2 |  |  | 有功状态 | 1 | I16 | 4001 | - |  | V_APStateToPPM
3 |  |  | 有功3秒均值 | 1 | I32 | 4002-4003 | W |  | V_GridRealPower3Sec
4 |  |  | 当前可利用功率 | 1 | I32 | 4004-4005 | W |  | V_AvailablePowerToPPM
5 |  |  | 额定功率 | 1 | I32 | 4006-4007 | W |  | P_RatedPower
6 |  |  | 当前有功限值 | 1 | I32 | 4008-4009 | W |  | V_PM_ActivePowerSetpointW
7 |  |  | 累计有功发电量 | 1 | I32 | 4010-4011 | kWh |  | S_TotalProduction
8 |  |  | 累计发电时间 | 1 | I32 | 4012-4013 | s |  | S_TotalOperation
9 |  |  | 当前风速3秒均值 | 1 | I16 | 4014 | 0.1m/s |  | V_WindSpeed3Sec
10 |  |  | PPM有功通讯中断间隔限值 | 1 | I32 | 4015-4016 | S | 该值为设定PPM有功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5007故障 | P_APComChangeTime
11 |  |  | 可利用功率10分钟平均值上限 | 1 | I32 | 4017-4018 | W |  | V_AvailablePowerToPPM10MinAver
12 |  |  | 预留 |  | I32 | 4019-4020
13 |  | 无功 | 无功握手信号 | 1 | I16 | 4021 | - |  | V_SentToPPMRPCount
14 |  |  | 无功状态 | 1 | I16 | 4022 | - |  | V_RPStateToPPM
15 |  |  | 无功3秒均值 | 1 | I32 | 4023-4024 | kVar |  | V_GridReactivePower3Sec
16 |  |  | PPM无功通讯中断间隔限值 | 1 | I32 | 4025-4026 | S | 该值为设定PPM无功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5008故障 | P_RPComChangeTime
17 |  |  | 当前无功限值 | 1 | I32 | 4027-4028 | Var |  | V_PM_ReactivePowerSetpoint
18 | PPM to Turbine | 有功 | PPM有功握手信号 | 1 | I16 | 4029 | - |  | V_APCountFromPPM
19 |  |  | PPM有功控制模式 | 1 | I16 | 4030 | - |  | V_APStateFromPPM
20 |  |  | 有功设定值 | 1 | I32 | 4031-4032 | W |  | V_ActivePowerSetpoint
21 |  |  | 预留 |  | I32 | 4033-4034
22 |  | 无功 | PPM无功握手信号 | 1 | I16 | 4035 | - |  | V_RPCountFromPPM
23 |  |  | PPM无功控制模式 | 1 | I16 | 4036 | - |  | V_RPStateFromPPM
24 |  |  | 无功设定值 | 1 | I32 | 4037-4038 | Var |  | V_ReactivePowerSetpoint
25 |  |  | 预留 |  | I32 | 4039-4040
26 |  |  | 预留 |  | I32 | 4041-4042
27 | Safety Chain |  | 安全链状态 | 1 | I16 | 100 | 字符串 | 1:"EStop Error" 2:"SC1 Error" 3:"SC2 Error" 4:"Safety Ok" | V_SafetyChainStateText
28 |  |  | 安全链故障 | 1 | I16 | 101 | 字符串 | 1:"Detecting..." 2:"Emergency Stop Nacelle Ext." 3:"Emergency Stop Nacelle" 4:"Emergency Stop Tower Base" 5:"EStop Awaiting reset" 6:"SafetyChain MCB" 7:"Vibration" 8:"WP2035 (R) Overspeed" 9:"WP2035 (G) Overspeed" 10:"SC1 Awaiting reset" 11:"Manual Safety Stop Nacelle" 12:"WP4000 Controller relay" 13:"SC2 Awaiting reset" 14:"None" | V_SafetyChainErrorText
29 |  |  | 安全链复位模式 | 1 | I16 | 102 | 字符串 | 1:"OFF" 2:"MANUAL" 3:"AUTOMATIC" 4:"ON" 5:"UNKNOWN" | V_ResetModeText
30 |  |  | 上电复位模式 | 1 | I16 | 103 | 字符串 | 1:"Done" 2:"Executing" 3:"None" 4:"Pending" | V_ResetOnBootText
31 |  |  | 机舱急停按钮状态 | 1 | I16 | 104 | 0/1 | The current condition on input | DI_EmergencyStopNacelleExternal
32 |  |  | 机舱柜急停按钮状态 | 1 | I16 | 105 | 0/1 | The current condition on input | DI_EmergencyStopNacellePanel
33 |  |  | 塔基急停按钮状态 | 1 | I16 | 106 | 0/1 | The current condition on input | DI_EmergencyStopTowerBase
34 |  |  | 急停继电器状态 | 1 | I16 | 107 | 0/1 | The current condition on input | DI_EmergencyStopRelay
35 |  |  | 安全链总状态 | 1 | I16 | 108 | 0/1 | The current condition on input | DI_SafetyChainMCCB
36 |  |  | 振动开关状态 | 1 | I16 | 109 | 0/1 | The current condition on input | DI_VibrationSensor
37 |  |  | 安全链继电器1状态 | 1 | I16 | 110 | 0/1 | The current condition on input | DI_SafetyChainRelayOne
38 |  |  | WP2035主轴超速模块状态 | 1 | I16 | 111 | 0/1 | Shows the rotor wp2035 overspeed detection, the current condition on input | DI_FeedbackRotorOverspeed
39 |  |  | WP2035发电机超速模块状态 | 1 | I16 | 112 | 0/1 | Shows the generator wp2035 overspeed detection, the current condition on input | DI_FeedbackGeneratorOverspeed
40 |  |  | 机舱柜安全停机 | 1 | I16 | 113 | 0/1 | The current condition on input | DI_SafetyChainManualStopNacelle
41 |  |  | WP4100安全链输入信号 | 1 | I16 | 114 | 0/1 | The current condition on input | Chain_In_Signal
42 |  |  | WP4100安全链输出信号 | 1 | I16 | 115 | 0/1 | The current condition on input | Chain_Out_Signal
43 |  |  | 变桨安全链状态 | 1 | I16 | 116 | 0/1 | The current condition on input | DI_SafetyChainRelayTwo
44 |  |  | 安全链继电器2状态 | 1 | I16 | 117 | 0/1 | The current condition on input | DI_SafetyChainRelayTwo
45 |  |  | 塔基手动停机 | 1 | I16 | 118 | 0/1 | The current condition on input | DI_ManualStopTowerBase
46 |  |  | 机舱手动停机 | 1 | I16 | 119 | 0/1 | The current condition on input | DI_ManualStopNacelle
47 |  |  | 手动停止顺时针偏航 | 1 | I16 | 120 | 0/1 | The current condition on input | DI_YawEndStopCw
48 |  |  | 手动停止逆时针偏航 | 1 | I16 | 121 | 0/1 | The current condition on input | DI_YawEndStopCcw
49 |  |  | 本地复位安全链信号 | 1 | I16 | 122 | 0/1 | The current condition on input | DI_SafetyChainResetPulse
50 |  |  | 远程复位安全链信号 | 1 | I16 | 123 | 0/1 | The current condition on output | DO_ResetSafetyChain
51 | Operate |  | 机组运行状态 | 1 | I16 | 200 | 字符串 | 1:"Starting" 2:"Service" 3:"Yaw into wind" 4:"Selftest run check" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Freewheel init" 12:"Freewheel G1" 13:"Grid connect G1" 14:"Operation G1" 15:"LVRT" 16:"Freewheel G1G1" 17:"Battery test" 18:"Pitch Service Test" 19:"B200" 20:"B199" 21:"B99" 22:"B50" 23:"None" | V_ActualOperateStateTxt
52 |  |  | 运行状态剩余时间 | 1000 | I32 | 201-202 | s | Up/down counter estimating the time until the end of this state. When it is zero, the state changes. Shows the lowest of the timers, except in the starting state where the highest one is shown. | V_EventTimeOut
53 |  |  | 计时名称 | 1 | I16 | 203 | 字符串 | 1:"Secs until start" 2:"Force start" 3:"Start wind" 4:"Brake cool" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Gen.rpm OK" 12:"State timeout" 13:"Connect window" 14:"Phase Drop" 15:"Power Recovery" 16:"None" | V_ActualOperateTimerTxt
54 |  |  | 运行步骤 | 1 | I16 | 204 | 字符串 | 1:"None" 2:"Waiting for MDS" 3:"Waiting for Grid" 4:"STEP 1" 5:"STEP 2" 6:"STEP 3" 7:"STEP 4" 8:"STEP 5" | V_ActualOperateStepTxt
55 |  |  | 运行模式 | 1 | I16 | 205 | 字符串 | 1:"RUN-AUTO" 2:"RUN-SERVICE" 3:"SERVICE" 4:"UNKNOWN" | V_OperateModeText
56 |  |  | 变桨模式 | 1 | I16 | 206 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"ESTOP" 4:"UNKNOWN" | V_PitchModeText
57 |  |  | 变频器模式 | 1 | I16 | 207 | 字符串 | 1:"RUN" 2:"STOP" 3:"UNKNOWN" | V_InverterModeText
58 |  |  | 变桨MDS模式 | 1 | I16 | 208 | 字符串 | 1:"SAFETY" 2:"OPERATE" 3:"SERVICE" 4:"BATTERYTEST1" 5:"BATTERYTEST2" 6:"BATTERYTEST3" 7:"TEST" 8:"SIMULATE" 9:"UNKNOWN" | V_MDSModeText
59 |  |  | 变桨位置极限 | 100 | I32 | 209-210 | ° | Min. allowed pitch angle, sent to Pitch Controller | V_PitchPositionLimit
60 |  |  | 变桨速度极限 | 100 | I32 | 211-212 | °/s | Max. allowed pitch speed, sent to Pitch Controller | V_PitchSpeedLimit
61 |  |  | 发电机转速极限 | 100 | I32 | 213-214 | rpm | Max. allowed generator rpm, sent to Pitch Controller. | V_GeneratorRpmLimit
62 |  |  | 转矩极限 | 10 | I32 | 215-216 | Nm | Max. allowed torque, sent to Torque Controller. | V_TorqueLimit
63 |  |  | 制动冷却时间 | 1000 | I32 | 217-218 | S | Time until brakes have been cooled down after applying. When 0 the turbine can be started. This timer uses value from the parameter Brake Cool xxx s p. 169. The timer can be used as state timer in the operational state Starting (see 2.6.2.2). The timer counts down to 0 if mechanical brake is released (3.3#16 "HYDRAULIC VALVE BRAKER OPEN" p. 658 = 0) or if "Zero rpm" ( Rotor xxxxxxxx.xxx rpm p. 331 < 2 rpm and Generator xxxxxxxx.x rpm p. 306 < 2 rpm * Gear Ratio xxx.xx p. 351) is reached. | V_BrakeCoolTime
63+ |  |  | 当前首故障 | 1 | I16 | 219 | / |  | V_ActiveCP1CodeNo
63++ |  |  | 当前故障数量 | 1 | I16 | 220 | / |  | V_NofActiveStatusCodes
64 | Turbine Status |  | 风机限功状态 | 1 | I16 | 3200 | 0/1 |  | V_PowerReducedOperation
65 |  |  | 风机发电状态 | 1 | I16 | 3201 | 0/1 |  | V_ToPM_P_GridConnect
66 |  |  | 风机待机状态 | 1 | I16 | 3202 | 0/1 |  | V_WT_StandbyMode
67 |  |  | 风机停机状态 | 1 | I16 | 3203 | 0/1 |  | V_WT_Stopstatus
68 |  |  | 风机维护状态 | 1 | I16 | 3204 | 0/1 |  | V_WT_Servicestatus
69 |  |  | 机组有功功率设定值（可写） | 1000 | I32 | 3205-3206 | kw |  | B_ToPM_P_Sp_kW
70 |  |  | 机组无功功率设定值（可写） | 1000 | I32 | 3207-3208 | kVAr |  | B_ToPM_Q_Sp_kVAr
71 |  |  | 机组控制(可写) | 1 | I16 | 3209 | - | 1：启动 2：停止 3：复位 | V_RemoteCommand
72 | Yaw |  | 当前偏航程序 | 1 | I16 | 300 | / | Shows the active yaw program (0,30,50,60, 70, 80, 100, 230 or 240). | V_ActiveControlProgram2
73 |  |  | 当前偏航状态 | 1 | I16 | 301 | 字符串 | 1:"STOPPED" 2:"START CW" 3:"STARTCCW" 4:"RUN. CW" 5:"STOPPING" 6:"RUN. CCW" 7:"STOPPING" | V_ActualYawStateTxt
74 |  |  | 偏航自动模式 | 1 | I16 | 302 | 0/1 |  | DI_YawAutomodeSwitch
75 |  |  | 顺时针解缆限位开关 | 1 | I16 | 303 | 0/1 | The current condition on input | DI_YawEndStopCw
76 |  |  | 逆时针解缆限位开关 | 1 | I16 | 304 | 0/1 | The current condition on input | DI_YawEndStopCcw
77 |  |  | 顺时针偏航 | 1 | I16 | 305 | 0/1 | The current condition on output | DO_YawMotorCw
78 |  |  | 顺时针偏航继电器反馈 | 1 | I16 | 306 | 0/1 | The current condition on input | DI_YawMotorCWContactor
79 |  |  | 逆时针偏航 | 1 | I16 | 307 | 0/1 | The current condition on output | DO_YawMotorCcw
80 |  |  | 逆时针偏航继电器反馈 | 1 | I16 | 308 | 0/1 | The current condition on input | DI_YawMotorCCWContactor
81 |  |  | 偏航系统供电回路反馈 | 1 | I16 | 309 | 0/1 | The current condition on input | DI_MCBYawSystemFB
82 |  |  | 偏航半压制动 | 1 | I16 | 310 | 0/1 | The current condition on output | DO_MechanicalYawReduceBrakeValve
83 |  |  | 偏航全压制动 | 1 | I16 | 311 | 0/1 | The current condition on output | DO_MechanicalYawFullBrakeValve
84 |  |  | 偏航电磁制动 | 1 | I16 | 312 | 0/1 | The electrical yaw brake | DO_YawBrakeelectrical
85 |  |  | 机舱相对正北角度 | 10 | I16 | 313 | ° | Shows the position of the nacelle in context to a circle were 0°is North. | V_NacelleDirection
86 |  |  | 机舱相对风向角度 | 10 | I16 | 314 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned correctly according to the wind direction. | V_RelaWindVaneDirection3Sec
87 |  |  | 偏航传感器A | 1 | I16 | 315 | 0/1 | The current condition on input | DI_YawCountSensorA
88 |  |  | 偏航传感器B | 1 | I16 | 316 | 0/1 | The current condition on input | DI_YawCountSensorB
89 |  |  | 解缆传感器（0=逆时针/1=顺时针） | 1 | I16 | 317 | 0/1 | Shows which way the cable is twisted (1 = Cw / 0 = Ccw). | DI_YawCableTwist
90 |  |  | 解缆角度 | 10 | I32 | 318-319 | ° | Shows how many degrees the cables in the tower are twisted. To reset the value | V_NacelleTwistDeg
91 |  |  | 偏航程序模式 | 1 | I16 | 320 | 0/1 | Shows the active yaw program. | V_YawParameterSet
92 |  |  | 顺时针偏航倒计时 | 1000 | I32 | 321-322 | s | Yaw delay for the CW direction. | V_StartYawCwDelay
93 |  |  | 逆时针偏航倒计时 | 1000 | I32 | 323-324 | s | Yaw delay for the CCW direction. | V_StartYawCcwDelay
94 | Pitch |  | 功率设定值 | 1000 | I32 | 502-503 | KW | Power setpoint from Operate to the PID controller | V_PitchPowerSetpoint
95 |  |  | 变桨角度 | 100 | I32 | 504-505 | ° | Simple average of the actual 3 pitch angles. | V_PitchAngle
96 |  |  | 变桨角度设定值 | 100 | I32 | 506-507 | ° | Angle Setpoint sent to the Blade controller | V_PitchCtrl_AngleSetPoint
97 |  |  | 变桨速度 | 100 | I32 | 508-509 | °/s | Pitch speed. | V_PitchAngleSpeed
98 |  |  | PID输入模式 | 1 | I16 | 510 | 字符串 | 1:"SPEED" 2:"AUTO" | V_PID_ModeTxt
99 |  |  |  | 1 | I16 | 511 | 字符串 | 1:"ENABLED" 2:"DISABLED" | V_RippleDamperEnableTxt
100 |  |  |  | 1 | I16 | 512 | 字符串 | 1:"ENABLED" 2:"DISABLED" | V_ZeroPointDamperEnableTxt
101 | Blade Controller |  | 变桨当前模式 | 1 | I16 | 600 | 字符串 | 1:"Safety" 2:"Operate" 3:"Service" 4:"Batterytest1" 5:"Batterytest2" 6:"Batterytest3" 7:"Test mode" 8:"Simulate Pitch" | V_MDSCurrentModeTxt
102 |  |  | 变桨速度限值 | 100 | I32 | 601-602 | ° | Pitch speed limit from the pitch regulator. | V_PitchSpeedLimit
103 |  |  | 变桨角度设定值 | 100 | I32 | 603-604 | ° |  | V_PitchAngleSetPoint
104 |  |  | 1号桨叶角度 | 100 | I32 | 605-606 | ° | Actual pitch angle blade 1. | V_MDSActPitchAngleA
105 |  |  | 2号桨叶角度 | 100 | I32 | 607-608 | ° | Actual pitch angle blade 2. | V_MDSActPitchAngleB
106 |  |  | 3号桨叶角度 | 100 | I32 | 609-610 | ° | Actual pitch angle blade 3. | V_MDSActPitchAngleC
107 |  |  | 1号桨叶当前故障 | 1 | I16 | 611 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults1
108 |  |  | 2号桨叶当前故障 | 1 | I16 | 612 | / | Lists active faults on Blade 2. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults2
109 |  |  | 3号桨叶当前故障 | 1 | I16 | 613 | / | Lists active faults on Blade 3. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults3
110 |  |  | 1号桨叶当前报警 | 1 | I16 | 614 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings1
111 |  |  | 2号桨叶当前报警 | 1 | I16 | 615 | / | Lists active warnings on Blade 2. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings2
112 |  |  | 3号桨叶当前报警 | 1 | I16 | 616 | / | Lists active warnings on Blade 3. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings3
113 |  |  | Modbus驱动器控制 | 1 | I16 | 617 | 字符串 | 1:"Run" 2:"Config" | V_ModbusMasterControlTxt
114 |  |  | 1号桨叶MDS通讯OK | 1 | I16 | 618 | 0/1 | Indicates communication status towards Blade 1. | V_Unit1NodeDead
115 |  |  | 2号桨叶MDS通讯OK | 1 | I16 | 619 | 0/1 | Indicates communication status towards Blade 2. | V_Unit2NodeDead
116 |  |  | 3号桨叶MDS通讯OK | 1 | I16 | 620 | 0/1 | Indicates communication status towards Blade 3. | V_Unit3NodeDead
117 |  |  | 复位变桨通讯状态（可写） | 1 | I16 | 621 | 0/1 | This setting must be updated to 1 to reset MDS communication related statistics. After the update the setting will automatically return to 0. | V_MDSResetCommStats
118 |  |  | 通讯信息 | 1 | I16 | 622 | / |  | V_MDS_BrcMsgsTx
119 |  |  | MDS1读取的请求数量 | 1 | I16 | 623 | / | Number of read requests sent. | V_ReadReqTx_Unit1
120 |  |  | MDS1收到的响应数量 | 1 | I16 | 624 | / | Number of received reponses. | V_ResponseRx_Unit1
121 |  |  | MDS1丢失的响应数量 | 1 | I16 | 625 | / | Number of missing responses. | V_MissingResponse_Unit1
122 |  |  | CRC故障 | 1 | I16 | 626 | / |  | V_CrcErrors_Unit1
123 |  |  | MDS1结构故障数量 | 1 | I16 | 627 | / | Number of responses received containing framing errors. | V_FrameErrors_Unit1
124 |  |  | MDS2读取的请求数量 | 1 | I16 | 628 | / | Number of read requests sent. | V_ReadReqTx_Unit1
125 |  |  | MDS2收到的响应数量 | 1 | I16 | 629 | / | Number of received reponses. | V_ResponseRx_Unit2
126 |  |  | MDS2丢失的响应数量 | 1 | I16 | 630 | / | Number of missing responses. | V_MissingResponse_Unit2
127 |  |  | CRC故障 | 1 | I16 | 631 | / |  | V_CrcErrors_Unit2
128 |  |  | MDS2结构故障数量 | 1 | I16 | 632 | / | Number of responses received containing framing errors. | V_FrameErrors_Unit2
129 |  |  | MDS3读取的请求数量 | 1 | I16 | 633 | / | Number of read requests sent. | V_ReadReqTx_Unit1
130 |  |  | MDS3收到的响应数量 | 1 | I16 | 634 | / | Number of received reponses. | V_ResponseRx_Unit3
131 |  |  | MDS3丢失的响应数量 | 1 | I16 | 635 | / | Number of missing responses. | V_MissingResponse_Unit3
132 |  |  | CRC故障 | 1 | I16 | 636 | / |  | V_CrcErrors_Unit3
133 |  |  | MDS3结构故障数量 | 1 | I16 | 637 | / | Number of responses received containing framing errors. | V_FrameErrors_Unit3
134 |  |  | 变桨1软件版本 | 1 | I32 | 638-639 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | V_MDSSWVersionA
135 |  |  | 变桨1当前模式 | 1 | I16 | 640 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man." | V_MDSUnitACurrentModeTxt
136 |  |  | 变桨1以安全速度切出 | 1 | I16 | 641 | 字符串 | 1:"Normal" 2:"Safety" | V_MDS1SafetySpeedOut
137 |  |  | 变桨1当前故障 | 1 | I16 | 642 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults1
138 |  |  | 变桨1当前报警 | 1 | I16 | 643 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings1
139 |  |  | 变桨1电机状态 | 1 | I16 | 644 | 字符串 | 1:"Stopped" "Started" | V_MDS1MotorControl
140 |  |  | 变桨1制动状态 | 1 | I16 | 645 | 字符串 | 1:"Released" 2:"Activated" | V_MDS1BrakeControl
141 |  |  | 变桨1电池状态 | 1 | I16 | 646 | 字符串 | 1:"Disconnected" 2:"Connected" | V_MDS1BatteryControl
142 |  |  | 变桨1进程状态 | 1 | I16 | 647 | 字符串 | 1:"Disable" 2:"Enable" | V_MDS1Process
143 |  |  | 变桨1轮毂维护使能 | 1 | I16 | 648 | 0/1 | Specifies the hub service state on the MDS unit. | V_MDSHubServiceAEnabled
144 |  |  | 变桨2软件版本 | 1 | I32 | 649-650 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | V_MDSSWVersionB
145 |  |  | 变桨2当前模式 | 1 | I16 | 651 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man." | V_MDSUnitBCurrentModeTxt
146 |  |  | 变桨2以安全速度切出 | 1 | I16 | 652 | 字符串 | 1:"Normal" 2:"Safety" | V_MDS2SafetySpeedOut
147 |  |  | 变桨2当前故障 | 1 | I16 | 653 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults2
148 |  |  | 变桨2当前报警 | 1 | I16 | 654 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings2
149 |  |  | 变桨2电机状态 | 1 | I16 | 655 | 字符串 | 1:"Stopped" "Started" | V_MDS2MotorControl
150 |  |  | 变桨2制动状态 | 1 | I16 | 656 | 字符串 | 1:"Released" 2:"Activated" | V_MDS2BrakeControl
151 |  |  | 变桨2电池状态 | 1 | I16 | 657 | 字符串 | 1:"Disconnected" 2:"Connected" | V_MDS2BatteryControl
152 |  |  | 变桨2进程状态 | 1 | I16 | 658 | 字符串 | 1:"Disable" 2:"Enable" | V_MDS2Process
153 |  |  | 变桨2轮毂维护使能 | 1 | I16 | 659 | 0/1 | Specifies the hub service state on the MDS unit. | V_MDSHubServiceBEnabled
154 |  |  | 变桨3软件版本 | 1 | I32 | 660-661 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | V_MDSSWVersionC
155 |  |  | 变桨3当前模式 | 1 | I16 | 662 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man." | V_MDSUnitCCurrentModeTxt
156 |  |  | 变桨3以安全速度切出 | 1 | I16 | 663 | 字符串 | 1:"Normal" 2:"Safety" | V_MDS3SafetySpeedOut
157 |  |  | 变桨3当前故障 | 1 | I16 | 664 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults. | V_CurrentFaults3
158 |  |  | 变桨3当前报警 | 1 | I16 | 665 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings. | V_CurrentWarnings3
159 |  |  | 变桨3电机状态 | 1 | I16 | 666 | 字符串 | 1:"Stopped" "Started" | V_MDS3MotorControl
160 |  |  | 变桨3制动状态 | 1 | I16 | 667 | 字符串 | 1:"Released" 2:"Activated" | V_MDS3BrakeControl
161 |  |  | 变桨3电池状态 | 1 | I16 | 668 | 字符串 | 1:"Disconnected" 2:"Connected" | V_MDS3BatteryControl
162 |  |  | 变桨3进程状态 | 1 | I16 | 669 | 字符串 | 1:"Disable" 2:"Enable" | V_MDS3Process
163 |  |  | 变桨3轮毂维护使能 | 1 | I16 | 670 | 0/1 | Specifies the hub service state on the MDS unit. | V_MDSHubServiceCEnabled
164 |  |  | 上一次电池测试2/3时间 | 1 | I64 | 671-674 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix | B_MDSLastBatteryTest2Time
165 |  |  | 1号桨叶上一次电池测试电压 | 1 | I16 | 675 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 1. | B_MDSBatteryVoltageA
166 |  |  | 2号桨叶上一次电池测试电压 | 1 | I16 | 676 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 2. | B_MDSBatteryVoltageB
167 |  |  | 3号桨叶上一次电池测试电压 | 1 | I16 | 677 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 3. | B_MDSBatteryVoltageC
168 |  |  | 电池测试请求信号 | 1 | I16 | 678 | 0/1 | The MDS system has requested the operation program to perform a battery test 2 or 3. | V_MDSRequestBatteryTest
169 |  |  | 手动电池测试请求（可写） |  | I16 | 679 | 0/1 |  | V_MDSManualRequestBatteryTest
170 |  |  | 电池测试故障 | 1 | I16 | 680 | 0/1 | Indicates if the latest battery test failed. A successfull battery test is required before the turbine is allowed to start. | B_MDSBatteryTestFailed
171 | Torque |  | 转矩控制器状态 | 1 | I16 | 700 | 字符串 | 1:"OFF (Limited to 0Nm)" 2:"L PI Grid Connect X.Ys" 3:"L PI Ramp Lower Limit" 4:"L PI Ramp to G1G1" 5:"L PI Active" 6:"Speed Ctrl. Await Torque" 7:"Critical Torque" 8:"Critical Torque" 9:"Power-Speed Red. ZkW" 10:"Power Red. ZkW" 11:"Power Control Rated Power" 12:"Speed Ctrl. Await Op. RPM SP" 13:"Exiting Power Control" 14:"Torque Table Lookup" | V_TorqueStateText
172 |  |  | 转矩设定值 | 10 | I32 | 701-702 | Nm | Torque Setpoint calculated by the torque controller | V_TorqueSPNm
173 |  |  | 转矩设定百分比 | 100 | I16 | 703 | % | Shows torque setpoint in percents | V_TorqueSetpointPct
174 |  |  | 发电机转速 | 100 | I32 | 704-705 | rpm |  | V_LocalControlRpm
175 |  |  | PI控制器的发电机转速设定值 | 100 | I32 | 706-707 | rpm | Generator speed setpoint for the torque PI controller. See section 2.10.1.2 for details. | V_GenRpm_SP
176 |  |  | 发电机额定转速设定值 | 100 | I32 | 708-709 | rpm | Operational Speed setpoint. This is the rated speed of the turbine. See Operate object for details. | V_OperationSpeedSP
177 |  |  | 最小转矩限值百分比 | 100 | I32 | 710-711 | rpm | Define the dynamic minimum torque to be applied. See section 2.10.1.2 for details | V_TorqueLowerPct
178 |  |  | 最大转矩限值百分比3 | 100 | I32 | 712-713 | rpm | Define the dynamic maximum torque to be applied. See section 2.10.1.2 for details. | V_TorqueUpperPct
179 |  |  | 转矩基值 | 10 | I32 | 714-715 | Nm | Baseline used for the torque PI controllers. See section 2.10.2 for details. | V_TorqueBaseLine
180 |  |  | 转矩基值百分比 | 100 | I16 | 716 | % | Baseline used for the torque PI controllers. See section 2.10.2 for details | V_TorqueBaseLinePct
181 |  |  | 网侧功率 | 1000 | I32 | 717-718 | kw | Active power measured by the control system and exponential averaged by Power Average Time x.xx s p. 246. | V_GridSidePower3SecAvg
182 |  |  | 发电机功率 | 1000 | I32 | 719-720 | kw | Calculated active power on the generator and exponential averaged by Power Average Time x.xx s p. 246. | V_TorqueCalcPower3Sec
183 |  |  | 机组消耗功率 | 1000 | I32 | 721-722 | kw | Estimate of auxiliaries consumption to be compensated by the torque controller in Power Control Mode. See section 2.10.3 for details. | V_PowerLossDynamic
184 |  |  | 机械效率 | 1000 | I32 | 723-724 | / | Efficiency based on lookup table Mech. Efficiency Table p. 241 | V_TorqueMechEfficiency
185 | Inverter |  | 变频器模式 | 1 | I16 | 800 | 字符串 | 1:"Reset" 2:"Stopped" 3:"Run" 4:"Grid Connected" | V_InverterModeTxt
186 |  |  | 发电机转速（编码器） | 10 | I16 | 801 | rpm | Actual speed of the generator. | V_InverterSpeedAct
187 |  |  | 转矩 | 100 | I16 | 802 | % | Actual Generator torque in percentage | V_InverterTorqueAct
188 |  |  | 控制字 | 1 | I16 | 803 | / |  | V_InverterControlWord
189 |  |  | ON(bit 0) | 1 | I16 | 804 | 0/1 |  | V_InverterControlWordOn
190 |  |  | RUN(bit 3) | 1 | I16 | 805 | 0/1 |  | V_InverterControlWordRun
191 |  |  | RESET(bit 7） | 1 | I16 | 806 | 0/1 |  | V_InverterControlWordReset
192 |  |  | 有功功率 | 10 | I16 | 807 | kW | Actual power. | V_InverterPowerAct
193 |  |  | 无功功率 | 10 | I16 | 808 | kvar | Actual reactive power. | V_InverterkVArAct
194 |  |  | 直流母线电压 | 10 | I16 | 809 | V | Mains voltage. | V_InverterUGrid
195 |  |  | 直流母线电流 | 10 | I16 | 810 | A | Line curreunt. | V_InverterIGrid
196 |  |  | 变频器PP温度 | 1 | I16 | 811 | °C | PP temperature in degrees centigrade. | V_InverterPpTemp
197 |  |  | 变频器制动器 | 1 | I16 | 812 | 0/1 | Shows the status of the inverter brealer on 1.4#31 "Inverter Breaker" p. 545 (0 = Error, 1 = OK) | DI_InverterBreaker
198 |  |  | 转矩变化率 | 100 | I16 | 813 | % | Torque setpoint used to control the inverter. | V_InverterTorqueRef
199 |  |  | 相角变化率 | 100 | I16 | 814 | ° |  | V_InverterPhiRef
200 | LVRT |  | LVRT上一次触发时间 | 1 | I64 | 1400-1403 | / | The time stamp of the last LVRT situation | V_TorqueLVRT_DropStartTimeStamp
201 |  |  | LVRT上一次持续时间 | 1 | I32 | 1404-1405 | ms | The duration time of the last LVRT situation | V_TorqueLVRT_DropDurationTime
202 | Generator |  | 发电机转速（主控） | 100 | I32 | 900-901 | rpm | Generator rpm. | AI_GeneratorRpm
203 |  |  | 发电机转速1秒平均值 | 100 | I32 | 902-903 | rpm | Shows the 1 sec. averaged rotor speed | V_GeneratorRpm1Sec
204 |  |  | 发电机转速30秒平均值 | 100 | I32 | 904-905 | rpm | Shows the 30 sec. averaged rotor speed | V_GeneratorRpm30Sec
205 |  |  | 发电机转速10分钟平均值 | 100 | I32 | 906-907 | rpm | Shows the 600 sec. averaged rotor speed | V_GeneratorRpm10Min
206 |  |  | 发电机加热器模式 | 1 | I16 | 908 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenHeatModeText
207 |  |  | 发电机滑环室加热模式 | 1 | I16 | 909 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenSRHeatModeText
208 |  |  | 发电机风扇电机加热模式 | 1 | I16 | 910 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenFansHeatModeText
209 |  |  | 发电机冷却模式 | 1 | I16 | 911 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenCoolerModeText
210 |  |  | 发电机滑环室冷却模式 | 1 | I16 | 912 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF" | V_GenSRCoolerModeText
211 |  |  | 发电机频率 | 1000 | I32 | 913-914 | Hz | Shows the generator speed in Hz. | AI_GeneratorRpmFrq
212 |  |  | 发电机L1绕组温度 | 10 | I16 | 915 | °C | Shows the (G) stator winding L1 temperature. | PT_TempGenCoilL1
213 |  |  | 发电机L2绕组温度 | 10 | I16 | 916 | °C | Shows the (G) stator winding L2 temperature. | PT_TempGenCoilL2
214 |  |  | 发电机L3绕组温度 | 10 | I16 | 917 | °C | Shows the (G) stator winding L3 temperature. | PT_TempGenCoilL3
215 |  |  | 发电机驱动端轴承温度 | 10 | I16 | 918 | °C | Shows the (G) bearing DE temperature. | PT_GeneratorBearingDETemp
216 |  |  | 发电机非驱动端轴承温度 | 10 | I16 | 919 | °C | Shows the (G) bearing NDE temperature. | PT_GeneratorBearingNDETemp
217 |  |  | 发电机加热器状态 | 1 | I16 | 920 | 0/1 | The current condition on output 3.2#14 "Heating Generator" p. 550 (0 = Heating OFF, 1 = Heating ON). | DO_GeneratorHeating
218 |  |  | 发电机滑环室加热器状态 | 1 | I16 | 921 | 0/1 |  | DO_GeneratorSRHeater
219 |  |  | 发电机风扇加热器状态 | 1 | I16 | 922 | 0/1 |  | DO_GeneratorFansHeater
220 |  |  | 发电机加热器反馈 | 1 | I16 | 923 | 0/1 | Heating feedback signal 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK). | DI_FBFuseHeaters
221 |  |  | 发电机前置风扇反馈 | 1 | I16 | 924 | 0/1 | The current condition on output 3.2#16 "Generator Fan Front" p. 550 (0 = Fan OFF, 1 = Fan ON). | DO_GeneratorFanFront
222 |  |  | 发电机顶部风扇反馈 | 1 | I16 | 925 | 0/1 | The current condition on output 3.2#17 "Generator Fan Top" p. 550 (0 = Fan OFF, 1 = Fan ON). | DO_GeneratorFanTop
223 |  |  | 发电机滑环室风扇反馈 | 1 | I16 | 926 | 0/1 |  | DO_GeneratorSRFans
224 |  |  | 发电机风扇断路器反馈 | 1 | I16 | 927 | 0/1 | The current state of the fan feedback on 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK). | DI_FeedbackMCB
225 |  |  | 发电机碳刷报警 | 1 | I16 | 928 | 0/1 | The current state of the brush wear on 3.3#41 "Generator Brush Wear Error" p. 555 (0 = ERROR, 1 = OK). | DI_GeneratorBrushWearError
226 |  |  | 发电机风扇出口温度 | 10 | I16 | 929 | °C | Shows the (G) fan outer temperature. | PT_GeneratorFanOuterTemp
227 |  |  | 发电机滑环室温度 | 10 | I16 | 930 | °C |  | PT_SlipRingTemperature
228 | Power Management |  | 功率控制模式 | 1 | I16 | 2900 | 字符串 | 1:"No Red. Active" 2:"Local, kW" 3:"Local, %" 4:"Remote" 5:"12345678901234567890" 6:"Freq. drop active" 7:"Grid: High Freq." 8:"Low Limit Active" | V_PM_StatusString
229 |  |  | 有功功率设定值 | 1000 | I32 | 2901-2902 | kW | Shows the requested active power production. | V_PM_ActivePowerSetpointW
230 |  |  | 有功功率1秒平均值 | 1000 | I32 | 2903-2904 | kW | Active Power 1s xxxxx.x kW | V_GridRealPower1Sec
231 |  |  | 有功功率10分钟平均值 | 1000 | I32 | 2905-2906 | kW | 10 minute average value of active power production. | V_GridRealPower10Min
232 |  |  | 无功功率设定值 | 1000 | I32 | 2907-2908 | kvar | Shows the requested reactive power. | V_PM_ReactivePowerSetpoint
233 |  |  | 无功功率1秒平均值 | 1000 | I32 | 2909-2910 | kvar | 1 second average value of reactive power production or consumption. | V_GridReactivePower1Sec
234 |  |  | 无功功率10分钟平均值 | 1000 | I32 | 2911-2912 | kvar | 10 minute average value of reactive power production or consumption. | V_GridReactivePower10Min
235 | Brake Disk |  | 制动模式 | 1 | I16 | 400 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"UNKNOWN" | V_BrakeModeText
236 |  |  | 制动类型 | 1 | I16 | 401 | 字符串 | 1:"OPEN" 2:"CLOSE" 3:"AUTO CLOSE" 4:"UNKNOWN" | V_BrakeTypeText
237 |  |  | 制动盘报警 | 1 | I16 | 402 | 0/1 | The current condition on input | DI_BrakePadsOneWornOut
238 |  |  | 液压制动松闸（0=抱闸/1=松闸） | 1 | I16 | 403 | 0/1 | The current condition on input | DO_HydraulicValveBrakerOpen
239 |  |  | 主轴制动释放 | 1 | I16 | 404 | 0/1 | 3.2-51# | TI_RotorBrakeReleased
240 |  |  | 主轴制动抱闸 | 1 | I16 | 405 | 0/1 | 3.2-52# | TI_RotorBrakeLocked
241 |  |  | 主轴转速设定值 | 100 | I32 | 500-501 | rpm | Speed setpoint from Operate to the PID controller. | V_OperateCtrl_RotorSpeedSetpoint
242 | Rotor |  | 主轴转速 | 100 | I32 | 1000-1001 | rpm | Rotor rpm. | AI_RotorRpm
243 |  |  | 主轴轴承1温度 | 10 | I16 | 1002 | °C | The current temperature on PT100 input 3.3#69+ "Spindle Bearing 1" p. 620 | PT_SpindleBearing1
244 |  |  | 主轴轴承2温度 | 10 | I16 | 1003 | °C | The current temperature on PT100 input 3.3#70+ "Spindle Bearing 2" p. 620 | PT_SpindleBearing2
245 |  |  | 主轴软件超速 | 1 | I16 | 1004 | 0/1 | The current condition on input (0 = OK, 1 = Error). | DI_FeedbackRotorOverspeed
246 |  |  | 液压站过滤器堵塞 | 1 | I16 | 1005 | 0/1 | The current condition on input 3.3#46 "Hydraulic Filter Blocked" p. 555 (1 = Error, 0 = OK). Used in status code 441 - Brake pressure p. 270 | DI_HydraulicPressLimitSwitchRotorBrakeLow
247 |  |  | 主轴刹车抱闸 | 1 | I16 | 1006 | 0/1 | The current condition on input 3.2#51 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 85 bar. | TI_RotorBrakeLocked
248 |  |  | 主轴刹车释放 | 1 | I16 | 1007 | 0/1 | The current condition on input 3.2#52 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 10 bar. | TI_RotorBrakeReleased
249 |  |  | 主轴锁定销1释放 | 1 | I16 | 1008 | 0/1 | The current condition on input 3.2#46 "Rotor Unlock 1" p. 551 (1 = Released, 0 = Locked). | DI_RotorLock1
250 |  |  | 主轴锁定销2释放 | 1 | I16 | 1009 | 0/1 | The current condition on input 3.2#47 "Rotor Unlock 2" p. 551 (1 = Released, 0 = Locked) | DI_RotorLock2
251 |  |  | 滑环加热器断路器反馈 | 1 | I16 | 1010 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK). | DI_FBFuseHeaters
252 |  |  | 主轴转速1秒平均值 | 100 | I32 | 1011-1012 | rpm | Shows the 1 sec. averaged rotor speed | V_RotorRpm1Sec
253 |  |  | 主轴转速30秒平均值 | 100 | I32 | 1013-1014 | rpm | Shows the 30 sec. averaged rotor speed | V_RotorRpm30Sec
254 |  |  | 主轴转速10分钟平均值 | 100 | I32 | 1015-1016 | rpm | Shows the 600 sec. averaged rotor speed | V_RotorRpm10Min
255 |  |  | 主轴频率 | 1000 | I32 | 1017-1018 | Hz | Shows the rotor frequency from the sensor | AI_RotorRpmFrq
256 | Gear |  | 齿轮箱润滑油过滤器压力反馈 | 1 | I16 | 1100 | 0/1 | The current gear oil filter pressure 3.3#43 "Gear Oil Presssure Status" p. 618. | DI_GearOilPresssureStatus
257 |  |  | 齿轮箱过滤器堵塞 | 1 | I16 | 1101 | 0/1 | Filter clogged on 3.3#33 "Gear Box Filter Blooding" p. 618 (1 = clogged, 0 = OK). | DI_GearBoxFilterBlooding
258 |  |  | 齿轮箱润滑油油位 | 1 | I16 | 1102 | 0/1 | The current Gear oil level on 3.3#42 "Gear Oil Level/SNK" p. 555 (0=Err, 1=OK). | DI_GearOilLevelSNK
259 |  |  | 齿轮箱润滑油风扇 | 1 | I16 | 1103 | 0/1 | The current condition on output 3.3#8 "Gear Oil Cooling" p. 554 (0=Off, 1=On). | DO_GearOilCoolerHighSpeed
260 |  |  | 齿轮箱润滑油油泵和风扇断路器反馈 | 1 | I16 | 1104 | 0/1 | The current condition on output 3.3#26 "Feedback MCB Gear Box Oil Pump & Gear Oil Cooler" p. 555 (0=Err, 1=Ok). | DI_FeedbackMcbGearOilPumpAndCooler
261 |  |  | 齿轮箱润滑油加热器 | 1 | I16 | 1105 | 0/1 | The current condition on output 3.2#8 "Gear Oil Heating" p. 550 (0=Off, 1=On). | DO_GearOilHeating
262 |  |  | 齿轮箱加热器反馈 | 1 | I16 | 1106 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0=Err, 1=Ok). | DI_FBFuseHeaters
263 |  |  | 齿轮箱润滑油泵高速 | 1 | I16 | 1107 | 0/1 | The current condition on output 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 (0=Off, 1=On). | DO_GearBoxOilPumpHighSpeed
264 |  |  | 齿轮箱润滑油泵低速 | 1 | I16 | 1108 | 0/1 | The current condition on output 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 (0=Off, 1=On). | DO_GearBoxOilPumpLowSpeed
265 |  |  | 齿轮箱风扇电机加热器 | 1 | I16 | 1109 | 0/1 | The current condition on output 3.3#10 "Gear Box Cooler Motor Heater" p. 554 (0=Off, 1=On). This output is set high if 3.3#8 "Gear Oil Cooling" p. 554 is 0. | DO_GearBoxCoolerMotorHeater
266 |  |  | 齿轮箱油泵加热器 | 1 | I16 | 1110 | 0/1 | The current condition on output 3.2#19 "Gear Box Pump Heater" p. 551 (0=Off, 1=On). This output is set high if 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 and 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 both are 0. | DO_GearBoxPumpHeater
267 |  |  | 齿轮箱油温 | 10 | I16 | 1111 | °C | This parameter shows the actual measured temperature of the gear oil on on 3.3#65+ "Gear Box Oil Temp." p. 556. | PT_GearBoxOilTemperature
268 |  |  | 齿轮箱油泵温度 | 10 | I16 | 1112 | °C | The current Gear pump oil temperature on 3.3#66+ "Gear Pump Oil Temp." p. 557. | PT_GearOilPumpTemp
269 |  |  | 齿轮箱轴承1温度 | 10 | I16 | 1113 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557. | PT_GearboxHighSpeedBearing1Temp
270 |  |  | 齿轮箱轴承2温度 | 10 | I16 | 1114 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557. | PT_GearboxHighSpeedBearing2Temp
271 |  |  | 齿轮箱进口油压 | 100 | I32 | 1115-1116 | bar | The current gear box import oil pressure on 3.2#64+ "Gear Box Import Oil Pressure" p. 552. | AI_GearImportOilPressure
272 |  |  | 过滤器进口油压 | 100 | I32 | 1117-1118 | bar | The current filter import oil pressure on 3.2#63+ "Filter Import Oil Pressure" p. 552. | AI_FilterImportOilPressure
273 | Grid |  | 电网电压 | 1 | I32 | 1200-1201 | V | The average of the three measured "Line to neutral"-voltages | AI_GridVoltage
274 |  |  | 电网电流 | 1 | I16 | 1202 | A | The average current for all three lines. | AI_GridCurrent
275 |  |  | 电网频率 | 1000 | I32 | 1203-1204 | Hz | The grid frequency measured by the grid module | V_GridFrequencyLog
276 |  |  | 电网有功功率 | 1000 | I32 | 1205-1206 | kW | The active power measured by the grid module | AI_GridRealPower
277 |  |  | 电网无功功率 | 1000 | I32 | 1207-1208 | kVAr | The reactive power measured by the grid module. | AI_GridReactivePower
278 |  |  | 电网功率因数 | 1000 | I16 | 1209 | / | The power factor calculated by the grid module | AI_GridCosPhi
279 |  |  | 电网L1相电压 | 1 | I32 | 1210-1211 | V | The L1 Voltage "Line to Neutral" measured by the grid module | AI_GridL1Voltage
280 |  |  | 电网L2相电压 | 1 | I32 | 1212-1213 | V | The L2 Voltage "Line to Neutral" measured by the grid module. | AI_GridL2Voltage
281 |  |  | 电网L3相电压 | 1 | I32 | 1214-1215 | V | The L3 Voltage "Line to Neutral" measured by the grid module. | AI_GridL3Voltage
282 |  |  | 电网L1相电流 | 1 | I16 | 1216 | A | The current on L1 measured by the grid module. | AI_GridL1Current
283 |  |  | 电网L2相电流 | 1 | I16 | 1217 | A | The current on L2 measured by the grid module. | AI_GridL2Current
284 |  |  | 电网L3相电流 | 1 | I16 | 1218 | A | The current on L3 measured by the grid module. | AI_GridL3Current
285 |  |  | 电网L1/L2相位角 | 1000 | I32 | 1219-1220 | ° | The phase angle between L1-L2. | AI_GridL1L2PhaseShift
286 |  |  | 电网L1/L3相位角 | 1000 | I32 | 1221-1222 | ° | The phase angle between L1-L3 | AI_GridL1L3PhaseShift
287 |  |  | 有功功率100毫秒平均值 | 1000 | I32 | 1223-1224 | KW |  | V_GridRealPower100ms
288 |  |  | 有功功率1秒平均值 | 1000 | I32 | 1225-1226 | KW |  | V_GridRealPower1Sec
289 |  |  | 有功功率3秒平均值 | 1000 | I32 | 1227-1228 | KW |  | V_GridRealPower3Sec
290 |  |  | 有功功率30秒平均值 | 1000 | I32 | 1229-1230 | KW |  | V_GridRealPower30Sec
291 |  |  | 有功功率10分钟平均值 | 1000 | I32 | 1231-1232 | KW |  | V_GridRealPower10Min
292 |  |  | 无功功率100毫秒平均值 | 1000 | I32 | 1233-1234 | kvar |  | V_GridReactivePower100ms
293 |  |  | 无功功率1秒平均值 | 1000 | I32 | 1235-1236 | kvar |  | V_GridReactivePower1Sec
294 |  |  | 无功功率3秒平均值 | 1000 | I32 | 1237-1238 | kvar |  | V_GridReactivePower3Sec
295 |  |  | 无功功率30秒平均值 | 1000 | I32 | 1239-1240 | kvar |  | V_GridReactivePower30Sec
296 |  |  | 无功功率10分钟平均值 | 1000 | I32 | 1241-1242 | kvar |  | V_GridReactivePower10Min
297 |  |  | L1相电压互感器变比 | 1000 | I32 | 1243-1244 | / |  | V_GridL1VoltageGain
298 |  |  | L2相电压互感器变比 | 1000 | I32 | 1245-1246 | / |  | V_GridL2VoltageGain
299 |  |  | L3相电压互感器变比 | 1000 | I32 | 1247-1248 | / |  | V_GridL3VoltageGain
300 |  |  | L1相电流互感器变比 | 1000 | I32 | 1249-1250 | / |  | V_GridL1CurrentGain
301 |  |  | L2相电流互感器变比 | 1000 | I32 | 1251-1252 | / |  | V_GridL2CurrentGain
302 |  |  | L3相电流互感器变比 | 1000 | I32 | 1253-1254 | / |  | V_GridL3CurrentGain
303 |  |  | 电网L1相峰值电压 | 1 | I32 | 1255-1256 | V | The highest voltage measured on L1 based on "Line to Neutral". | S_GridL1VoltagePeak
304 |  |  | 电网L1相峰值电压发生时间 | 1 | I64 | 1257-1260 | / | This menuline shows the timestamp for when the voltage peak, see Peak Volt. L1 x V p. 332, occured. | B_PeakTimeGridVoltL1
305 |  |  | 电网L2相峰值电压 | 1 | I32 | 1261-1262 | V | The highest voltage measured on L2 based on "Line to Neutral". | S_GridL2VoltagePeak
306 |  |  | 电网L2相峰值电压发生时间 | 1 | I64 | 1263-1266 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L2 x V p. 332, occured. | B_PeakTimeGridVoltL2
307 |  |  | 电网L3相峰值电压 | 1 | I32 | 1267-1268 | V | The highest voltage measured on L3 based on "Line to Neutral". | S_GridL3VoltagePeak
308 |  |  | 电网L3相峰值电压发生时间 | 1 | I64 | 1269-1272 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L3 x V p. 332, occured. | B_PeakTimeGridVoltL3
309 |  |  | 电网L1相峰值电流 | 1 | I32 | 1273-1274 | A | The highest current measured on L1 | S_GridL1CurrentPeak
310 |  |  | 电网L1相峰值电流发生时间 | 1 | I64 | 1275-1278 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L1 x A p. 332, occured. | B_PeakTimeGridCurrentL1
311 |  |  | 电网L2相峰值电流 | 1 | I32 | 1279-1280 | A | The highest current measured on L2. | S_GridL2CurrentPeak
312 |  |  | 电网L2相峰值电流发生时间 | 1 | I64 | 1281-1284 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L2 x A p. 333, occured. | B_PeakTimeGridCurrentL2
313 |  |  | 电网L3相峰值电流 | 1 | I32 | 1285-1286 | A | The highest current measured on L3 | S_GridL3CurrentPeak
314 |  |  | 电网L3相峰值电流发生时间 | 1 | I64 | 1287-1290 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L3 x A p. 333, occured. | B_PeakTimeGridCurrentL3
315 |  |  | 电网L1相最大正向矢量波动值 | 1000 | I32 | 1291-1292 | ° | The highest positive peak vector surge on L1. | S_GridL1VectorSurgePositivePeak
316 |  |  | 电网L1相最大正向矢量波动值发生时间 | 1 | I64 | 1293-1296 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L1 x.x ° p. 333, has occured. | B_PeakTimeGridVSPosL1
317 |  |  | 电网L2相最大正向矢量波动值 | 1000 | I32 | 1297-1298 | ° | The highest positive peak vector surge on L2. | S_GridL2VectorSurgePositivePeak
318 |  |  | 电网L2相最大正向矢量波动值发生时间 | 1 | I64 | 1299-1302 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L2 x.x ° p. 333, has occured. | B_PeakTimeGridVSPosL2
319 |  |  | 电网L3相最大正向矢量波动值 | 1000 | I32 | 1303-1304 | ° | The highest positive peak vector surge on L3 | S_GridL3VectorSurgePositivePeak
320 |  |  | 电网L3相最大正向矢量波动值发生时间 | 1 | I64 | 1305-1308 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L3 x.x ° p. 334, has occured | B_PeakTimeGridVSPosL3
321 |  |  | 电网L1相最大负向矢量波动值 | 1000 | I32 | 1309-1310 | ° | The highest negative peak vector surge on L1 | S_GridL1VectorSurgeNegativePeak
322 |  |  | 电网L1相最大负向矢量波动值发生时间 | 1 | I64 | 1311-1314 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L1 x.x ° p. 334, has occured. | B_PeakTimeGridVSNegL1
323 |  |  | 电网L2相最大负向矢量波动值 | 1000 | I32 | 1315-1316 | ° | The highest negative peak vector surge on L2 | S_GridL2VectorSurgeNegativePeak
324 |  |  | 电网L2相最大负向矢量波动值发生时间 | 1 | I64 | 1317-1320 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L2 x.x ° p. 334, has occured. | B_PeakTimeGridVSNegL2
325 |  |  | 电网L3相最大负向矢量波动值 | 1000 | I32 | 1321-1322 | ° | The highest negative peak vector surge on L3. | S_GridL3VectorSurgeNegativePeak
326 |  |  | 电网L3相最大负向矢量波动值发生时间 | 1 | I64 | 1323-1326 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L3 x.x ° p. 334, has occured. | B_PeakTimeGridVSNegL3
327 | Hydraulic |  | 液压站状态 | 1 | I16 | 1500 | 字符串 | 1:"Blocked" 2:"Service On" 3:"Service Off" 4:"Auto" | V_HydraulicPumpStateTxt
328 |  |  | 液压站油泵状态 | 1 | I16 | 1501 | 0/1 | The current condition on 3.2#7 "Hydraulic pump" p. 550 (0 = Off, 1 = On). | DO_HydraulicPump
329 |  |  | 液压站油泵过载（0=Error/1=OK） | 1 | I16 | 1502 | 0/1 | The current condition on input 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK). | DI_FeedbackMCB
330 |  |  | 液压站油位 | 1 | I16 | 1503 | 0/1 | The current condition on input 3.3#38 "Hydraulic Oil Level" p. 555 (0 = Low, 1 = OK). | DI_HydraulicOilLevel
331 |  |  | 液压站温度高（>70） | 1 | I16 | 1504 | 0/1 | The current condition on input 3.3#28 "Hydraulic Temp. High (>=70 °C)" p. 555 (0 = OK, 1 = High). | DI_HydraulicTempHighGreaterThan70
332 |  |  | 液压站系统压力（1=OK/0=Low） | 1 | I16 | 1505 | 0/1 | The current pressure condition on input 3.3#44 "Hydraulic System Pressure Motor Start (Position 40)" p. 555 (1 = OK, 0 = Low). | DI_HydraulicSystemPressureMotorStart
333 |  |  | 液压站系统压力（1=OK/0=High） | 1 | I16 | 1506 | 0/1 | The current pressure condition on input 3.3#45 "" p. 555 (1 = OK, 0 = High). | DI_HydraulicSystemPressure
334 |  |  | 液压站压力 | 100 | I32 | 1507-1508 | bar | The current condition on the scaled input 3.2#62+ "Hydraulic Pressure" p. 552 (in bar). | AI_HydraulicPressure
335 | PT100 |  | 反馈点1.4.65信号错误 | 1 | I16 | 1600 | 0/1 |  | V_TowerControlBoxControlTemp_Err
336 |  |  | 反馈点1.4.66信号错误 | 1 | I16 | 1601 | 0/1 |  | V_TowerBaseTemp_Err
337 |  |  | 反馈点1.4.67信号错误 | 1 | I16 | 1602 | 0/1 |  | V_TransformerTemp1_Err
338 |  |  | 反馈点1.4.68信号错误 | 1 | I16 | 1603 | 0/1 |  | V_TransformerTemp2_Err
339 |  |  | 反馈点1.4.69信号错误 | 1 | I16 | 1604 | 0/1 |  | V_OutdoorTemperature_Err
340 |  |  | 反馈点3.2.65信号错误 | 1 | I16 | 1605 | 0/1 |  | V_TempNacelle_Err
341 |  |  | 反馈点3.2.66信号错误 | 1 | I16 | 1606 | 0/1 |  | V_ControlPanelTemp_Err
342 |  |  | 反馈点3.2.67信号错误 | 1 | I16 | 1607 | 0/1 |  | V_SlipRingTemp_Err
343 |  |  | 反馈点3.2.68信号错误 | 1 | I16 | 1608 | 0/1 |  | V_TempGenCoilL1_Err
344 |  |  | 反馈点3.2.69信号错误 | 1 | I16 | 1609 | 0/1 |  | V_TempGenCoilL2_Err
345 |  |  | 反馈点3.2.70信号错误 | 1 | I16 | 1610 | 0/1 |  | V_TempGenCoilL3_Err
346 |  |  | 反馈点3.2.71信号错误 | 1 | I16 | 1611 | 0/1 |  | V_TempGenBearingDE_Err
347 |  |  | 反馈点3.2.72信号错误 | 1 | I16 | 1612 | 0/1 |  | V_TempGenBearingNDE_Err
348 |  |  | 反馈点3.3.65信号错误 | 1 | I16 | 1613 | 0/1 |  | V_GearOilTemperature_Err
349 |  |  | 反馈点3.3.66信号错误 | 1 | I16 | 1614 | 0/1 |  | V_GearOilPumpTemp_Err
350 |  |  | 反馈点3.3.67信号错误 | 1 | I16 | 1615 | 0/1 |  | V_GearboxHighSpeedBearing1Temp_Err
351 |  |  | 反馈点3.3.68信号错误 | 1 | I16 | 1616 | 0/1 |  | V_GearboxHighSpeedBearing2Temp_Err
352 |  |  | 反馈点3.3.69信号错误 | 1 | I16 | 1617 | 0/1 |  | V_SpindleBearingOne_Err
353 |  |  | 反馈点3.3.70信号错误 | 1 | I16 | 1618 | 0/1 |  | V_SpindleBearingTwo_Err
354 |  |  | 反馈点3.3.72信号错误 | 1 | I16 | 1619 | 0/1 |  | V_GenFanOutterTemp_Err
355 | 4-20mA |  | 反馈点3.2.62信号错误 | 1 | I16 | 1700 | 0/1 |  | V_HydraulicPressureCurrent_Err
356 |  |  | 反馈点3.2.63信号错误 | 1 | I16 | 1701 | 0/1 |  | V_FilterImportOilPressureCurrent_Err
357 |  |  | 反馈点3.3.61信号错误 | 1 | I16 | 1702 | 0/1 |  | V_WindDirectionOneCurrent_Err
358 |  |  | 反馈点3.3.62信号错误 | 1 | I16 | 1703 | 0/1 |  | V_WindDirectionTwoCurrent_Err
359 | Anemometer |  | 3秒平均风速 | 100 | I16 | 1800 | m/s | This shows the 3 sec. averaged wind speed. | V_WindSpeed3Sec
360 |  |  | 30秒平均风速 | 100 | I16 | 1801 | m/s | This shows the 30 sec. averaged wind speed | V_WindSpeed30Sec
361 |  |  | 10分钟平均风速 | 100 | I16 | 1802 | m/s |  | V_WindSpeed10Min | 5月16日新增
362 |  |  | 当前使用的风速仪 | 1 | I16 | 1803 | / | This parameter shows the active anemometer. | V_WindSpeedActive
363 |  |  | 风速 | 100 | I16 | 1804 | m/s | This parameter shows the wind speed from the selected anemometer. | AI_WindSpeed
364 |  |  | 风速仪1实际反馈值 | 1000 | I32 | 1805-1806 | Hz |  | HSI_WindSpeedOne_Frq
365 |  |  | 风速仪2实际反馈值 | 1000 | I32 | 1807-1808 | Hz |  | HSI_WindSpeedTwo_Frq
366 | Wind Vane |  | 3秒平均风向 | 10 | I16 | 1900 | ° | Shows the 3 seconds averaged wind direction from the selected windvane. | V_WindVaneDirection3Sec
367 |  |  | 30秒平均风向 | 10 | I16 | 1901 | ° | Shows the 30 seconds averaged wind direction from the selected wind vane | V_WindVaneDirection30Sec
368 |  |  | 10分钟平均风速 | 10 | I16 | 1092 | ° |  | V_WindDirection10M | 5月16日新增
369 |  |  | 风向 | 10 | I16 | 1903 | ° | Shows the wind direction from the active wind vane. | AI_WindVaneDirection
370 |  |  | 机舱相对风向偏移量 | 10 | I16 | 1904 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned according to the correct wind direction. | V_RelaWindVaneDirection3Sec
371 |  |  | 机舱相对正北角度 | 10 | I16 | 1905 | ° | Shows the position of the nacelle seen in proportion to a circle where 0°is North. | V_NacelleDirection
372 |  |  | 当前使用的风向仪 | 1 | I32 | 1906-1907 | / | Shows which of the two wind vanes is currently active | V_WindVaneActiveVane
373 |  |  | 风向仪1相对正北角度 | 10 | I16 | 1908 | ° | Shows the wind direction seen in proportion to a circle where 0°is North. | V_WindDirection1
374 |  |  | 风向仪2相对正北角度 | 10 | I16 | 1909 | ° | Shows the wind direction 2 seen in proportion to a circle where 0°is North. | V_WindDirection2
375 |  |  | 风向仪1相对机舱角度 | 10 | I16 | 1910 | ° | Shows the wind vane 1 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection1
376 |  |  | 风向仪2相对机舱角度 | 10 | I16 | 1911 | ° | Shows the wind vane 2 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection2
377 |  |  | 风向仪1实际反馈值 | 1000 | I16 | 1912 | mA |  | AI_WindDirection1Current
378 |  |  | 风向仪2实际反馈值 | 1000 | I16 | 1913 | mA |  | AI_WindDirection2Current
379 | Outdoor |  | 测风仪加热器状态 | 1 | I16 | 2000 | 0/1 | The current condition on output 3.2#15 "Heating wind sensor" p. 550 (0 = Off, 1 = On). | DO_HeatingWindSensor
380 |  |  | 环境温度 | 10 | I16 | 2001 | °C | The measured environment temperature on input 1.4#69+ "Enviroment Temperature" p. 547. | PT_OutdoorTemp
381 | Lightning |  | 塔基柜内浪涌保护器 | 1 | I16 | 2100 | 0/1 | The current state of input 1.4#29 "Surge Protection (Tower Base)" p. 545. | DI_SurgeProtectionTowerBase
382 | Transformer |  | 箱变温度1 | 10 | I16 | 2200 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546). | PT_TransformerTemp1
383 |  |  | 箱变温度2 | 10 | I16 | 2201 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#68+ "Transfomer Temp. 2" p. 547). | PT_TransformerTemp2
384 |  |  | 35KV开关状态（0=OFF/1=ON） | 1 | I16 | 2202 | 0/1 | Shows the status of the 35 kV switch (Terminal 1.4#33 "Measuring open/close of the 35 kV switch" p. 545, 0 = OFF, 1 = ON). | DI_MeasOpenClose35kVSwitch
385 |  |  | 690V开关状态（0=OFF/1=ON） | 1 | I16 | 2203 | 0/1 | Shows the status of the 690 volt switch (Terminal 1.4#34 "Measuring open/close of the 0.69 kV switch" p. 545, 0 = OFF, 1 = ON). | DI_MeasOpenClose690VSwitch
386 |  |  | 箱变温度高 | 1 | I16 | 2204 | 0/1 |  | DI_TransformerTempHigh
387 |  |  | 箱变油位状态 | 1 | I16 | 2205 | 0/1 |  | DI_TransformerOilLevel
388 | Tower Base |  | 塔基温度 | 10 | I16 | 2400 | °C | Tower base temperature (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546) | PT_TowerBaseTemp
389 |  |  | 塔基烟雾报警 | 1 | I16 | 2401 | 0/1 |  | DI_TowerBaseSmokeDetection
390 | Ups |  | UPS通讯OK | 1 | I16 | 2500 | 0/1 | Communication status | V_UPSCommunicationOk
391 |  |  | UPS剩余时间 | 1 | I32 | 2501-2502 | s | The measured UPS remaining operation time with nominel load. The value is received through the serial connection to the UPS. In case of any communication error, the UPS remaining time is forced to zero. | V_UPSRemainingTime
392 |  |  | 机舱柜内浪涌保护器 | 1 | I16 | 2101 | 0/1 | The current state of input 3.3#50 "Surge Protection Nacelle" p. 555. | DI_SurgeProtectionTowerBase
393 | Air Pressure |  | 当前大气压力 | 1 | I16 | 2300 | mbar |  | V_AirPressure
394 |  |  | 1秒平均气压 | 1 | I16 | 2301 | mbar |  | V_AirPressure1Sec
395 |  |  | 30秒平均气压 | 1 | I16 | 2302 | mbar |  | V_AirPressure30Sec
396 |  |  | 10分钟平均气压 | 1 | I16 | 2303 | mbar |  | V_AirPressure10Min
397 | Vibration monitoring |  | 振动传感器1通道1值 | 1000 | I16 | 3000 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1 | V_WP4084No1VibOne
398 |  |  | 振动传感器1通道2值 | 1000 | I16 | 3001 | G | Shows the vibration level in sensor WP4084 No. 1, channel 2 | V_WP4084No1VibTwo
399 |  |  | 振动传感器1通道1+2值 | 1000 | I16 | 3002 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1 + channel 2 | V_WP4084No1VibOnePlusTwo
400 |  |  | 振动传感器1通道1状态 | 1 | I16 | 3003 | 0/1 | Shows the status of the WP4084 No. 1, channel 1 (0 = Ok, 1 = Vibration alarm, 2 = Selftest error). See section 2.39.5 for further details on sensor monitoring. | V_WP4084No1SensorOne
401 |  |  | 振动传感器1通道2状态 | 1 | I16 | 3004 | 0/1 | Shows the status of the sensor selftest (0 = Idle, 1 = Active). See section 2.39.4 for further details on sensor selftest. | V_WP4084No1SensorTwo
402 |  |  | 软件自检类型 | 1 | I16 | 3005 | 0/1 | Shows the selftest failure delay used by the sensor selftest software. (0 = 24 hours, 1 = 24 minutes). See section 2.39.4 for further details on sensor selftest. | V_WP4084No1SensorTest
403 |  |  | 振动传感器1通讯状态 | 1 | I16 | 3006 | 字符串 | 1:"Disabled" 2:"Error" 3:"Ok" | V_WP4084No1CommunicationTxt
404 | Flight Warning Light |  | 航空灯供电OK | 1 | I16 | 3100 | 0/1 | The current condition on input 3.3#36 "Supply Obstruction Lights 1 & 2 230V" p. 555 (0 = Error, 1 = Ok). | DI_FlightWarningLightSupplyOk
405 |  |  | 航空灯故障 | 1 | I16 | 3101 | 0/1 | The current condition on input 3.3#37 "Flight Warning Error" p. 555 (1 = Error, 0 = Ok). | DI_FlightWarningLightOk
406 | Lubrication |  | 发电机润滑油泵状态 | 1 | I16 | 2600 | 0/1 |  | DO_Lubrication_GeneratorBearingPump
407 |  |  | 轮毂轴承润滑油油位 | 1 | I16 | 2601 | 0/1 | The current condition on input 3.3#39 "Pitch Bearing Inner Ring Lubrication Grease Level" p. 555 (0 = Empty, 1 = OK). | DI_PitchBearInRingLubriGreaseLvl
408 |  |  | 轮毂轴承润滑油堵塞 | 1 | I16 | 2602 | 0/1 | The current condition on input 3.3#40 "Pitch Bearing Inner Ring Lubrication Blinding" p. 555 (Pulsing = OK, Not pulsing = Err). | DI_PitchBearInRingLubriBlind
409 |  |  | 轮毂润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2603 | 0/1 | The current condition on output 3.2#20 "Lubrication Pump Pitch System (Outer Ring)" p. 551 (0 = OFF, 1 = ON). | DO_LubriPumpPitchSystemRingIn
410 |  |  | 机舱轴承润滑油油位 | 1 | I16 | 2604 | 0/1 |  | DI_RotorBearLubriGreaseLvl
411 |  |  | 机舱轴承润滑油堵塞 | 1 | I16 | 2605 | 0/1 | The current condition on input 3.2#43 "Yaw Bear Lubrication Blinding" p. 551 (Pulsing = OK, Not pulsing = Err) | TI_YawBearLubricationBlind
412 |  |  | 机舱润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2606 | 0/1 | The current condition on output 3.3#9 "Yaw Lubrication Pump 1" p. 554 (0 = OFF, 1 = ON). | DO_YawLubricationPump1
413 | Nacelle |  | 机舱温度 | 10 | I16 | 2700 | °C | Nacelle temperature on PT100 input 3.2#65+ "Nacelle Temperature" p. 553. | PT_NacelleTemp
414 |  |  | 机舱风扇状态 | 1 | I16 | 2701 | 0/1 | Nacelle fan ON/OFF (output 3.2#18 "Nacelle Fan 1 & 2" p. 550). | DO_AirStreamSystem1_2
415 |  |  | 机舱风扇断路器反馈 | 1 | I16 | 2702 | 0/1 | Nacelle fan MCB FB ON/OFF (input 3.3#27 "Feedback MCB" p. 555). | DI_FeedbackMCB
416 |  |  | 机舱加热器1+2状态 | 1 | I16 | 2703 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF" | V_NacelleHeater1_2_Txt
417 |  |  | 机舱加热器3+4状态 | 1 | I16 | 2704 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF" | V_NacelleHeater3_4_Txt
418 |  |  | 机舱烟雾报警 | 1 | I16 | 2705 | 0/1 |  | DI_NacelleSmokeDetection
419 | Panels |  | 机舱柜温度 | 10 | I16 | 2800 | °C | Shows the status of the nacelle control panel temperature (Terminal 3.2#66+ "Nacelle Panel Temperature" p. 553). | PT_NacelleControlPanelTemp
420 |  |  | 塔基柜温度 | 10 | I16 | 2801 | °C | Shows the temperature of the tower base panel (Terminal 1.4#65+ "Tower Base Panel Temperature" p. 546). | PT_TowerBasePanelTemp
421 |  |  | 以太网开关OK | 1 | I16 | 2802 | 0/1 | Shows the status of the ethernet switch ES100 (Terminal 1.4#32 "Ethernet Switch ES100 OK" p. 545) | DI_EthernetSwitchOk
422 | 机组部件运行统计 |  | 顺时针偏航激活时长 | 10 | I64 | 3300-3303 | 小时 |  | DO_YawMotorCw
423 |  |  | 顺时针偏航激活次数 | 1 | I64 | 3304-3307 | 次
424 |  |  | 逆时针偏航激活时长 | 10 | I64 | 3308-3311 | 小时 |  | DO_YawMotorCcw
425 |  |  | 逆时针偏航激活次数 | 1 | I64 | 3312-3315 | 次
426 |  |  | 偏航电机激活时长 | 10 | I64 | 3316-3319 | 小时 |  | V_SumYawMotorActive
427 |  |  | 偏航电机激活次数 | 1 | I64 | 3320-3323 | 次
428 |  |  | 刹车盘抱闸时长 | 10 | I64 | 3324-3327 | 小时 |  | V_SumBrakeDisk
429 |  |  | 刹车盘抱闸次数 | 1 | I64 | 3328-3331 | 次
430 |  |  | 刹车盘施放时长 | 10 | I64 | 3332-3335 | 小时 |  | V_SumBrakeFree
431 |  |  | 刹车盘释放次数 | 1 | I64 | 3336-3339 | 次
432 |  |  | 发电机加热器工作时长 | 10 | I64 | 3340-3343 | 小时 |  | DO_GeneratorHeating
433 |  |  | 发电机加热器工作次数 | 1 | I64 | 3344-3347 | 次
434 |  |  | 发电机滑环室加热器工作时长 | 10 | I64 | 3348-3351 | 小时 |  | DO_GeneratorSRHeater
435 |  |  | 发电机滑环室加热器工作次数 | 1 | I64 | 3352-3355 | 次
436 |  |  | 发电机风扇电机加热器工作时长 | 10 | I64 | 3356-3359 | 小时 |  | DO_GeneratorFansHeater
437 |  |  | 发电机风扇电机加热器工作次数 | 1 | I64 | 3360-3363 | 次
438 |  |  | 发电机滑环室风扇工作时长 | 10 | I64 | 3364-3367 | 小时 |  | DO_GeneratorSRFans
439 |  |  | 发电机滑环室风扇工作次数 | 1 | I64 | 3368-3371 | 次
440 |  |  | 发电机风扇1工作时长 | 10 | I64 | 3372-3375 | 小时 |  | DO_GeneratorFanFront
441 |  |  | 发电机风扇1工作次数 | 1 | I64 | 3376-3379 | 次
442 |  |  | 发电机风扇2工作时长 | 10 | I64 | 3380-3383 | 小时 |  | DO_GeneratorFanTop
443 |  |  | 发电机风扇2工作次数 | 1 | I64 | 3384-3387 | 次
444 |  |  | 齿轮箱润滑油加热器工作时长 | 10 | I64 | 3388-3391 | 小时 |  | DO_GearOilHeating
445 |  |  | 齿轮箱润滑油加热器工作次数 | 1 | I64 | 3392-3395 | 次
446 |  |  | 齿轮箱风扇工作时长 | 10 | I64 | 3396-3399 | 小时 |  | DO_GearOilCoolerHighSpeed
447 |  |  | 齿轮箱风扇工作次数 | 1 | I64 | 3400-3403 | 次
448 |  |  | 齿轮箱油泵低速工作时长 | 10 | I64 | 3404-3407 | 小时 |  | DO_GearBoxOilPumpLowSpeed
449 |  |  | 齿轮箱油泵低速工作次数 | 1 | I64 | 3408-3411 | 次
450 |  |  | 齿轮箱油泵高速工作时长 | 10 | I64 | 3412-3415 | 小时 |  | DO_GearBoxOilPumpHighSpeed
451 |  |  | 齿轮箱油泵高速工作次数 | 1 | I64 | 3416-3419 | 次
452 |  |  | 液压站油泵工作时长 | 10 | I64 | 3420-3423 | 小时 |  | DO_HydraulicPump
453 |  |  | 液压站油泵工作次数 | 1 | I64 | 3424-3427 | 次
454 |  |  | 测风仪加热器工作时长 | 10 | I64 | 3428-3431 | 小时 |  | DO_HeatingWindSensor
455 |  |  | 测风仪加热器工作次数 | 1 | I64 | 3432-3435 | 次
456 | 电量统计 |  | 总发电量 | 1 | I64 | 3500-3503 | kWh |  | S_TotalProduction
457 |  |  | 总用电量 | 1 | I64 | 3504-3507 | kWh
458 |  |  | 日发电量 | 1 | I64 | 3508-3511 | kWh
459 |  |  | 日用电量 | 1 | I64 | 3512-3515 | kWh
460 |  |  | 周发电量 | 1 | I64 | 3516-3519 | kWh
461 |  |  | 周用电量 | 1 | I64 | 3520-3523 | kWh
462 |  |  | 月发电量 | 1 | I64 | 3524-3527 | kWh
463 |  |  | 月用电量 | 1 | I64 | 3528-3531 | kWh
464 |  |  | 年发电量 | 1 | I64 | 3532-3535 | kWh
465 |  |  | 年用电量 | 1 | I64 | 3536-3539 | kWh
466 | 时间统计 |  | 总发电时间 | 10 | I64 | 3540-3543 | 小时 |  | S_TotalOperation
467 |  |  | 日发电时间 | 10 | I64 | 3544-3547 | 小时
468 |  |  | 周发电时间 | 10 | I64 | 3548-3551 | 小时
469 |  |  | 月发电时间 | 10 | I64 | 3552-3555 | 小时
470 |  |  | 年发电时间 | 10 | I64 | 3556-3559 | 小时
471 |  |  | 总运行时间 | 10 | I64 | 3560-3563 | 小时 |  | S_Operate
472 |  |  | 日运行时间 | 10 | I64 | 3564-3567 | 小时
473 |  |  | 周运行时间 | 10 | I64 | 3568-3571 | 小时
474 |  |  | 月运行时间 | 10 | I64 | 3572-3575 | 小时
475 |  |  | 年运行时间 | 10 | I64 | 3576-3579 | 小时
476 |  |  | 总停机时间 | 10 | I64 | 3580-3583 | 小时 |  | S_OperationStopped
477 |  |  | 日停机时间 | 10 | I64 | 3584-3587 | 小时
478 |  |  | 周停机时间 | 10 | I64 | 3588-3591 | 小时
479 |  |  | 月停机时间 | 10 | I64 | 3592-3595 | 小时
480 |  |  | 年停机时间 | 10 | I64 | 3596-3599 | 小时
481 |  |  | 总启动风速时间 | 10 | I64 | 3600-3603 | 小时 |  | S_Startwind
482 |  |  | 日启动风速时间 | 10 | I64 | 3604-3607 | 小时
483 |  |  | 周启动风速时间 | 10 | I64 | 3608-3611 | 小时
484 |  |  | 月启动风速时间 | 10 | I64 | 3612-3615 | 小时
485 |  |  | 年启动风速时间 | 10 | I64 | 3616-3619 | 小时
486 | 风速统计 |  | 总平均风速 | 10 | I32 | 3620-3621 | m/s |  | S_WindspeedAvg
487 |  |  | 日平均风速 | 10 | I32 | 3622-3623 | m/s
488 |  |  | 周平均风速 | 10 | I32 | 3624-3625 | m/s
489 |  |  | 月平均风速 | 10 | I32 | 3626-3627 | m/s
490 |  |  | 年平均风速 | 10 | I32 | 3628-3629 | m/s
491 | 可利用率统计 |  | 总可利用率 | 100 | F32 | 3630-3631 | % |  | Availability
492 |  |  | 日可利用率 | 100 | F32 | 3632-3633 | %
493 |  |  | 周可利用率 | 100 | F32 | 3634-3635 | %
494 |  |  | 月可利用率 | 100 | F32 | 3636-3637 | %
495 |  |  | 年可利用率 | 100 | F32 | 3638-3639 | %

## PPM
序号 | 目录 |  | 名称 | Config |  |  | 单位 | 描述 | 变量名
|  |  |  | 倍数 | 数据类型 | 地址
1 | Turbine to PPM | 有功 | 有功握手信号 | 1 | I16 | 4000 | - |  | V_SentToPPMAPCount
2 |  |  | 有功状态 | 1 | I16 | 4001 | - |  | V_APStateToPPM
3 |  |  | 有功3秒均值 | 1 | I32 | 4002-4003 | W |  | V_GridRealPower3Sec
4 |  |  | 当前可利用功率 | 1 | I32 | 4004-4005 | W |  | V_AvailablePowerToPPM
5 |  |  | 额定功率 | 1 | I32 | 4006-4007 | W |  | P_RatedPower
6 |  |  | 当前有功限值 | 1 | I32 | 4008-4009 | W |  | V_PM_ActivePowerSetpointW
7 |  |  | 累计有功发电量 | 1 | I32 | 4010-4011 | kWh |  | S_TotalProduction
8 |  |  | 累计发电时间 | 1 | I32 | 4012-4013 | s |  | S_TotalOperation
9 |  |  | 当前风速3秒均值 | 1 | I16 | 4014 | 0.1m/s |  | V_WindSpeed3Sec
10 |  |  | PPM有功通讯中断间隔限值 | 1 | I32 | 4015-4016 | S | 该值为设定PPM有功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5007故障 | P_APComChangeTime
11 |  |  | 可利用功率10分钟平均值上限 | 1 | I32 | 4017-4018 | W |  | V_AvailablePowerToPPM10MinAver
12 |  |  | 预留 |  | I32 | 4019-4020
13 |  | 无功 | 无功握手信号 | 1 | I16 | 4021 | - |  | V_SentToPPMRPCount
14 |  |  | 无功状态 | 1 | I16 | 4022 | - |  | V_RPStateToPPM
15 |  |  | 无功3秒均值 | 1 | I32 | 4023-4024 | kVar |  | V_GridReactivePower3Sec
16 |  |  | PPM无功通讯中断间隔限值 | 1 | I32 | 4025-4026 | S | 该值为设定PPM无功通讯中断判定的参数值，当前PLC设定为3秒，即3秒后未接收到整数更新的话，报5008故障 | P_RPComChangeTime
17 |  |  | 当前无功限值 | 1 | I32 | 4027-4028 | Var |  | V_PM_ReactivePowerSetpoint
18 | PPM to Turbine | 有功 | PPM有功握手信号 | 1 | I16 | 4029 | - |  | V_APCountFromPPM
19 |  |  | PPM有功控制模式 | 1 | I16 | 4030 | - |  | V_APStateFromPPM
20 |  |  | 有功设定值 | 1 | I32 | 4031-4032 | W |  | V_ActivePowerSetpoint
21 |  |  | 预留 |  | I32 | 4033-4034
22 |  | 无功 | PPM无功握手信号 | 1 | I16 | 4035 | - |  | V_RPCountFromPPM
23 |  |  | PPM无功控制模式 | 1 | I16 | 4036 | - |  | V_RPStateFromPPM
24 |  |  | 无功设定值 | 1 | I32 | 4037-4038 | Var |  | V_ReactivePowerSetpoint
25 |  |  | 预留 |  | I32 | 4039-4040
26 |  |  | 预留 |  | I32 | 4041-4042

## 安全链
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 1 | Safety Chain | 安全链状态 | 1 | I16 | 100 | 字符串 | 1:"EStop Error" 2:"SC1 Error" 3:"SC2 Error" 4:"Safety Ok"
| 2 |  | 安全链故障 | 1 | I16 | 101 | 字符串 | 1:"Detecting..." 2:"Emergency Stop Nacelle Ext." 3:"Emergency Stop Nacelle" 4:"Emergency Stop Tower Base" 5:"EStop Awaiting reset" 6:"SafetyChain MCB" 7:"Vibration" 8:"WP2035 (R) Overspeed" 9:"WP2035 (G) Overspeed" 10:"SC1 Awaiting reset" 11:"Manual Safety Stop Nacelle" 12:"WP4000 Controller relay" 13:"SC2 Awaiting reset" 14:"None"
| 3 |  | 安全链复位模式 | 1 | I16 | 102 | 字符串 | 1:"OFF" 2:"MANUAL" 3:"AUTOMATIC" 4:"ON" 5:"UNKNOWN"
| 4 |  | 上电复位模式 | 1 | I16 | 103 | 字符串 | 1:"Done" 2:"Executing" 3:"None" 4:"Pending"
| 5 |  | 机舱急停按钮状态 | 1 | I16 | 104 | 0/1 | The current condition on input
| 6 |  | 机舱柜急停按钮状态 | 1 | I16 | 105 | 0/1 | The current condition on input
| 7 |  | 塔基急停按钮状态 | 1 | I16 | 106 | 0/1 | The current condition on input
| 8 |  | 急停继电器状态 | 1 | I16 | 107 | 0/1 | The current condition on input
1 | 9 |  | 安全链总状态 | 1 | I16 | 108 | 0/1 | The current condition on input
1 | 10 |  | 振动开关状态 | 1 | I16 | 109 | 0/1 | The current condition on input
1 | 11 |  | 安全链继电器1状态 | 1 | I16 | 110 | 0/1 | The current condition on input
1 | 12 |  | WP2035主轴超速模块状态 | 1 | I16 | 111 | 0/1 | Shows the rotor wp2035 overspeed detection, the current condition on input
1 | 13 |  | WP2035发电机超速模块状态 | 1 | I16 | 112 | 0/1 | Shows the generator wp2035 overspeed detection, the current condition on input
| 14 |  | 机舱柜安全停机 | 1 | I16 | 113 | 0/1 | The current condition on input
| 15 |  | WP4100安全链输入信号 | 1 | I16 | 114 | 0/1 | The current condition on input
| 16 |  | WP4100安全链输出信号 | 1 | I16 | 115 | 0/1 | The current condition on input
1 | 17 |  | 变桨安全链状态 | 1 | I16 | 116 | 0/1 | The current condition on input
1 | 18 |  | 安全链继电器2状态 | 1 | I16 | 117 | 0/1 | The current condition on input
| 19 |  | 塔基手动停机 | 1 | I16 | 118 | 0/1 | The current condition on input
| 20 |  | 机舱手动停机 | 1 | I16 | 119 | 0/1 | The current condition on input
| 21 |  | 手动停止顺时针偏航 | 1 | I16 | 120 | 0/1 | The current condition on input
| 22 |  | 手动停止逆时针偏航 | 1 | I16 | 121 | 0/1 | The current condition on input
| 23 |  | 本地复位安全链信号 | 1 | I16 | 122 | 0/1 | The current condition on input
| 24 |  | 远程复位安全链信号 | 1 | I16 | 123 | 0/1 | The current condition on output

## 运行
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
25 | Operate | 机组运行状态 | 1 | I16 | 200 | 字符串 | 1:"Starting" 2:"Service" 3:"Yaw into wind" 4:"Selftest run check" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Freewheel init" 12:"Freewheel G1" 13:"Grid connect G1" 14:"Operation G1" 15:"LVRT" 16:"Freewheel G1G1" 17:"Battery test" 18:"Pitch Service Test" 19:"B200" 20:"B199" 21:"B99" 22:"B50" 23:"None"
26 |  | 运行状态剩余时间 | 1000 | I32 | 201-202 | s | Up/down counter estimating the time until the end of this state. When it is zero, the state changes. Shows the lowest of the timers, except in the starting state where the highest one is shown.
27 |  | 计时名称 | 1 | I16 | 203 | 字符串 | 1:"Secs until start" 2:"Force start" 3:"Start wind" 4:"Brake cool" 5:"Selftest 1" 6:"Selftest 2" 7:"Selftest 3" 8:"Selftest 4" 9:"Selftest 5" 10:"Selftest skip" 11:"Gen.rpm OK" 12:"State timeout" 13:"Connect window" 14:"Phase Drop" 15:"Power Recovery" 16:"None"
28 |  | 运行步骤 | 1 | I16 | 204 | 字符串 | 1:"None" 2:"Waiting for MDS" 3:"Waiting for Grid" 4:"STEP 1" 5:"STEP 2" 6:"STEP 3" 7:"STEP 4" 8:"STEP 5"
29 |  | 运行模式 | 1 | I16 | 205 | 字符串 | 1:"RUN-AUTO" 2:"RUN-SERVICE" 3:"SERVICE" 4:"UNKNOWN"
30 |  | 变桨模式 | 1 | I16 | 206 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"ESTOP" 4:"UNKNOWN"
31 |  | 变频器模式 | 1 | I16 | 207 | 字符串 | 1:"RUN" 2:"STOP" 3:"UNKNOWN"
32 |  | 变桨MDS模式 | 1 | I16 | 208 | 字符串 | 1:"SAFETY" 2:"OPERATE" 3:"SERVICE" 4:"BATTERYTEST1" 5:"BATTERYTEST2" 6:"BATTERYTEST3" 7:"TEST" 8:"SIMULATE" 9:"UNKNOWN"
33 |  | 变桨位置极限 | 100 | I32 | 209-210 | ° | Min. allowed pitch angle, sent to Pitch Controller
34 |  | 变桨速度极限 | 100 | I32 | 211-212 | °/s | Max. allowed pitch speed, sent to Pitch Controller
35 |  | 发电机转速极限 | 100 | I32 | 213-214 | rpm | Max. allowed generator rpm, sent to Pitch Controller.
36 |  | 转矩极限 | 10 | I32 | 215-216 | Nm | Max. allowed torque, sent to Torque Controller.
37 |  | 制动冷却时间 | 1000 | I32 | 217-218 | S | Time until brakes have been cooled down after applying. When 0 the turbine can be started. This timer uses value from the parameter Brake Cool xxx s p. 169. The timer can be used as state timer in the operational state Starting (see 2.6.2.2). The timer counts down to 0 if mechanical brake is released (3.3#16 "HYDRAULIC VALVE BRAKER OPEN" p. 658 = 0) or if "Zero rpm" ( Rotor xxxxxxxx.xxx rpm p. 331 < 2 rpm and Generator xxxxxxxx.x rpm p. 306 < 2 rpm * Gear Ratio xxx.xx p. 351) is reached.
63+ |  | 当前首故障 | 1 | I16 | 219 | /
63++ |  | 当前故障数量 | 1 | I16 | 219 | /
386 | Turbine Status | 风机限功状态 | 1 | I16 | 3200 | 0/1
387 |  | 风机发电状态 | 1 | I16 | 3201 | 0/1
388 |  | 风机待机状态 | 1 | I16 | 3202 | 0/1
389 |  | 风机停机状态 | 1 | I16 | 3203 | 0/1
390 |  | 风机维护状态 | 1 | I16 | 3204 | 0/1
391 |  | 机组有功功率设定值（可写） | 1000 | I32 | 3205-3206 | kw
392 |  | 机组无功功率设定值（可写） | 1000 | I32 | 3207-3208 | kVAr
392+ |  | 机组控制(可写) | 1 | I16 | 3209 | - | 1：启动 2：停止 3：复位

## 偏航
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 38 | Yaw | 当前偏航程序 | 1 | I16 | 300 | / | Shows the active yaw program (0,30,50,60, 70, 80, 100, 230 or 240).
| 39 |  | 当前偏航状态 | 1 | I16 | 301 | 字符串 | 1:"STOPPED" 2:"START CW" 3:"STARTCCW" 4:"RUN. CW" 5:"STOPPING" 6:"RUN. CCW" 7:"STOPPING"
| 40 |  | 偏航自动模式 | 1 | I16 | 302 | 0/1
| 41 |  | 顺时针解缆限位开关 | 1 | I16 | 303 | 0/1 | The current condition on input
| 42 |  | 逆时针解缆限位开关 | 1 | I16 | 304 | 0/1 | The current condition on input
1 | 43 |  | 顺时针偏航 | 1 | I16 | 305 | 0/1 | The current condition on output
| 44 |  | 顺时针偏航继电器反馈 | 1 | I16 | 306 | 0/1 | The current condition on input
1 | 45 |  | 逆时针偏航 | 1 | I16 | 307 | 0/1 | The current condition on output
| 46 |  | 逆时针偏航继电器反馈 | 1 | I16 | 308 | 0/1 | The current condition on input
| 47 |  | 偏航系统供电回路反馈 | 1 | I16 | 309 | 0/1 | The current condition on input
| 48 |  | 偏航半压制动 | 1 | I16 | 310 | 0/1 | The current condition on output
| 49 |  | 偏航全压制动 | 1 | I16 | 311 | 0/1 | The current condition on output
| 50 |  | 偏航电磁制动 | 1 | I16 | 312 | 0/1 | The electrical yaw brake
1 | 51 |  | 机舱相对正北角度 | 10 | I16 | 313 | ° | Shows the position of the nacelle in context to a circle were 0°is North.
1 | 52 |  | 机舱相对风向角度 | 10 | I16 | 314 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned correctly according to the wind direction.
1 | 53 |  | 偏航传感器A | 1 | I16 | 315 | 0/1 | The current condition on input
1 | 54 |  | 偏航传感器B | 1 | I16 | 316 | 0/1 | The current condition on input
| 55 |  | 解缆传感器（0=逆时针/1=顺时针） | 1 | I16 | 317 | 0/1 | Shows which way the cable is twisted (1 = Cw / 0 = Ccw).
1 | 56 |  | 解缆角度 | 10 | I32 | 318-319 | ° | Shows how many degrees the cables in the tower are twisted. To reset the value
| 57 |  | 偏航程序模式 | 1 | I16 | 320 | 0/1 | Shows the active yaw program.
1 | 58 |  | 顺时针偏航倒计时 | 1000 | I32 | 321-322 | s | Yaw delay for the CW direction.
1 | 59 |  | 逆时针偏航倒计时 | 1000 | I32 | 323-324 | s | Yaw delay for the CCW direction.

## 变桨
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 67 | Pitch | 功率设定值 | 1000 | I32 | 502-503 | KW | Power setpoint from Operate to the PID controller
1 | 68 |  | 变桨角度 | 100 | I32 | 504-505 | ° | Simple average of the actual 3 pitch angles.
1 | 69 |  | 变桨角度设定值 | 100 | I32 | 506-507 | ° | Angle Setpoint sent to the Blade controller
1 | 70 |  | 变桨速度 | 100 | I32 | 508-509 | °/s | Pitch speed.
| 71 |  | PID输入模式 | 1 | I16 | 510 | 字符串 | 1:"SPEED" 2:"AUTO"
| 72 |  |  | 1 | I16 | 511 | 字符串 | 1:"ENABLED" 2:"DISABLED"
| 73 |  |  | 1 | I16 | 512 | 字符串 | 1:"ENABLED" 2:"DISABLED"
| 75 | Blade Controller | 变桨当前模式 | 1 | I16 | 600 | 字符串 | 1:"Safety" 2:"Operate" 3:"Service" 4:"Batterytest1" 5:"Batterytest2" 6:"Batterytest3" 7:"Test mode" 8:"Simulate Pitch"
| 76 |  | 变桨速度限值 | 100 | I32 | 601-602 | ° | Pitch speed limit from the pitch regulator.
1 | 77 |  | 变桨角度设定值 | 100 | I32 | 603-604 | °
1 | 78 |  | 1号桨叶角度 | 100 | I32 | 605-606 | ° | Actual pitch angle blade 1.
1 | 79 |  | 2号桨叶角度 | 100 | I32 | 607-608 | ° | Actual pitch angle blade 2.
1 | 80 |  | 3号桨叶角度 | 100 | I32 | 609-610 | ° | Actual pitch angle blade 3.
1 | 81 |  | 1号桨叶当前故障 | 1 | I16 | 611 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
1 | 82 |  | 2号桨叶当前故障 | 1 | I16 | 612 | / | Lists active faults on Blade 2. When a unit contains multiple active faults,the value toggles each second to display active faults.
1 | 83 |  | 3号桨叶当前故障 | 1 | I16 | 613 | / | Lists active faults on Blade 3. When a unit contains multiple active faults,the value toggles each second to display active faults.
1 | 84 |  | 1号桨叶当前报警 | 1 | I16 | 614 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
1 | 85 |  | 2号桨叶当前报警 | 1 | I16 | 615 | / | Lists active warnings on Blade 2. When a unit contains multiple active warnings the value toggles each second to display active warnings.
1 | 86 |  | 3号桨叶当前报警 | 1 | I16 | 616 | / | Lists active warnings on Blade 3. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 87 |  | Modbus驱动器控制 | 1 | I16 | 617 | 字符串 | 1:"Run" 2:"Config"
1 | 88 |  | 1号桨叶MDS通讯OK | 1 | I16 | 618 | 0/1 | Indicates communication status towards Blade 1.
1 | 89 |  | 2号桨叶MDS通讯OK | 1 | I16 | 619 | 0/1 | Indicates communication status towards Blade 2.
1 | 90 |  | 3号桨叶MDS通讯OK | 1 | I16 | 620 | 0/1 | Indicates communication status towards Blade 3.
| 91 |  | 复位变桨通讯状态（可写） | 1 | I16 | 621 | 0/1 | This setting must be updated to 1 to reset MDS communication related statistics. After the update the setting will automatically return to 0.
| 92 |  | 通讯信息 | 1 | I16 | 622 | /
| 93 |  | MDS1读取的请求数量 | 1 | I16 | 623 | / | Number of read requests sent.
| 94 |  | MDS1收到的响应数量 | 1 | I16 | 624 | / | Number of received reponses.
| 95 |  | MDS1丢失的响应数量 | 1 | I16 | 625 | / | Number of missing responses.
| 96 |  | CRC故障 | 1 | I16 | 626 | /
| 97 |  | MDS1结构故障数量 | 1 | I16 | 627 | / | Number of responses received containing framing errors.
| 98 |  | MDS2读取的请求数量 | 1 | I16 | 628 | / | Number of read requests sent.
| 99 |  | MDS2收到的响应数量 | 1 | I16 | 629 | / | Number of received reponses.
| 100 |  | MDS2丢失的响应数量 | 1 | I16 | 630 | / | Number of missing responses.
| 101 |  | CRC故障 | 1 | I16 | 631 | /
| 102 |  | MDS2结构故障数量 | 1 | I16 | 632 | / | Number of responses received containing framing errors.
| 103 |  | MDS3读取的请求数量 | 1 | I16 | 633 | / | Number of read requests sent.
| 104 |  | MDS3收到的响应数量 | 1 | I16 | 634 | / | Number of received reponses.
| 105 |  | MDS3丢失的响应数量 | 1 | I16 | 635 | / | Number of missing responses.
| 106 |  | CRC故障 | 1 | I16 | 636 | /
| 107 |  | MDS3结构故障数量 | 1 | I16 | 637 | / | Number of responses received containing framing errors.
| 108 |  | 变桨1软件版本 | 1 | I32 | 638-639 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 109 |  | 变桨1当前模式 | 1 | I16 | 640 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man."
| 110 |  | 变桨1以安全速度切出 | 1 | I16 | 641 | 字符串 | 1:"Normal" 2:"Safety"
| 111 |  | 变桨1当前故障 | 1 | I16 | 642 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
| 112 |  | 变桨1当前报警 | 1 | I16 | 643 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 113 |  | 变桨1电机状态 | 1 | I16 | 644 | 字符串 | 1:"Stopped" "Started"
| 114 |  | 变桨1制动状态 | 1 | I16 | 645 | 字符串 | 1:"Released" 2:"Activated"
| 115 |  | 变桨1电池状态 | 1 | I16 | 646 | 字符串 | 1:"Disconnected" 2:"Connected"
| 116 |  | 变桨1进程状态 | 1 | I16 | 647 | 字符串 | 1:"Disable" 2:"Enable"
| 117 |  | 变桨1轮毂维护使能 | 1 | I16 | 648 | 0/1 | Specifies the hub service state on the MDS unit.
| 118 |  | 变桨2软件版本 | 1 | I32 | 649-650 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 119 |  | 变桨2当前模式 | 1 | I16 | 651 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man."
| 120 |  | 变桨2以安全速度切出 | 1 | I16 | 652 | 字符串 | 1:"Normal" 2:"Safety"
| 121 |  | 变桨2当前故障 | 1 | I16 | 653 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
| 122 |  | 变桨2当前报警 | 1 | I16 | 654 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 123 |  | 变桨2电机状态 | 1 | I16 | 655 | 字符串 | 1:"Stopped" "Started"
| 124 |  | 变桨2制动状态 | 1 | I16 | 656 | 字符串 | 1:"Released" 2:"Activated"
| 125 |  | 变桨2电池状态 | 1 | I16 | 657 | 字符串 | 1:"Disconnected" 2:"Connected"
| 126 |  | 变桨2进程状态 | 1 | I16 | 658 | 字符串 | 1:"Disable" 2:"Enable"
| 127 |  | 变桨2轮毂维护使能 | 1 | I16 | 659 | 0/1 | Specifies the hub service state on the MDS unit.
| 128 |  | 变桨3软件版本 | 1 | I32 | 660-661 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 129 |  | 变桨3当前模式 | 1 | I16 | 662 | 字符串 | 1:"Startup" 2:"Safety Speed" 3:"Safety Stop" 4:"Fieldbus Broadcast Pos." 5:"Fieldbus Individual Pos." 6:"Keypad Speed" 7:"Keypad Pos." 8:"Service Box Speed" 9:"Service Box Pos." 10:"Special Program Auto" 11:"Special Program Man."
| 130 |  | 变桨3以安全速度切出 | 1 | I16 | 663 | 字符串 | 1:"Normal" 2:"Safety"
| 131 |  | 变桨3当前故障 | 1 | I16 | 664 | / | Lists active faults on Blade 1. When a unit contains multiple active faults,the value toggles each second to display active faults.
| 132 |  | 变桨3当前报警 | 1 | I16 | 665 | / | Lists active warnings on Blade 1. When a unit contains multiple active warnings the value toggles each second to display active warnings.
| 133 |  | 变桨3电机状态 | 1 | I16 | 666 | 字符串 | 1:"Stopped" "Started"
| 134 |  | 变桨3制动状态 | 1 | I16 | 667 | 字符串 | 1:"Released" 2:"Activated"
| 135 |  | 变桨3电池状态 | 1 | I16 | 668 | 字符串 | 1:"Disconnected" 2:"Connected"
| 136 |  | 变桨3进程状态 | 1 | I16 | 669 | 字符串 | 1:"Disable" 2:"Enable"
| 137 |  | 变桨3轮毂维护使能 | 1 | I16 | 670 | 0/1 | Specifies the hub service state on the MDS unit.
| 138 |  | 上一次电池测试2/3时间 | 1 | I64 | 671-674 | / | MDS unit software version. The software version is displayed as:major.minor.bugfix
| 139 |  | 1号桨叶上一次电池测试电压 | 1 | I16 | 675 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 1.
| 140 |  | 2号桨叶上一次电池测试电压 | 1 | I16 | 676 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 2.
| 141 |  | 3号桨叶上一次电池测试电压 | 1 | I16 | 677 | V | Shows the minimum battery voltage measured (during last battery test) on MDS unit 3.
| 142 |  | 电池测试请求信号 | 1 | I16 | 678 | 0/1 | The MDS system has requested the operation program to perform a battery test 2 or 3.
|  |  | 手动电池测试请求（可写） |  | I16 | 679 | 0/1
| 143 |  | 电池测试故障 | 1 | I16 | 680 | 0/1 | Indicates if the latest battery test failed. A successfull battery test is required before the turbine is allowed to start.

## 转矩
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 144 | Torque | 转矩控制器状态 | 1 | I16 | 700 | 字符串 | 1:"OFF (Limited to 0Nm)" 2:"L PI Grid Connect X.Ys" 3:"L PI Ramp Lower Limit" 4:"L PI Ramp to G1G1" 5:"L PI Active" 6:"Speed Ctrl. Await Torque" 7:"Critical Torque" 8:"Critical Torque" 9:"Power-Speed Red. ZkW" 10:"Power Red. ZkW" 11:"Power Control Rated Power" 12:"Speed Ctrl. Await Op. RPM SP" 13:"Exiting Power Control" 14:"Torque Table Lookup"
1 | 145 |  | 转矩设定值 | 10 | I32 | 701-702 | Nm | Torque Setpoint calculated by the torque controller
1 | 146 |  | 转矩设定百分比 | 100 | I16 | 703 | % | Shows torque setpoint in percents
1 | 147 |  | 发电机转速 | 100 | I32 | 704-705 | rpm
| 148 |  | PI控制器的发电机转速设定值 | 100 | I32 | 706-707 | rpm | Generator speed setpoint for the torque PI controller. See section 2.10.1.2 for details.
| 149 |  | 发电机额定转速设定值 | 100 | I32 | 708-709 | rpm | Operational Speed setpoint. This is the rated speed of the turbine. See Operate object for details.
| 150 |  | 最小转矩限值百分比 | 100 | I32 | 710-711 | rpm | Define the dynamic minimum torque to be applied. See section 2.10.1.2 for details
| 151 |  | 最大转矩限值百分比3 | 100 | I32 | 712-713 | rpm | Define the dynamic maximum torque to be applied. See section 2.10.1.2 for details.
| 152 |  | 转矩基值 | 10 | I32 | 714-715 | Nm | Baseline used for the torque PI controllers. See section 2.10.2 for details.
| 153 |  | 转矩基值百分比 | 100 | I16 | 716 | % | Baseline used for the torque PI controllers. See section 2.10.2 for details
1 | 154 |  | 网侧功率 | 1000 | I32 | 717-718 | kw | Active power measured by the control system and exponential averaged by Power Average Time x.xx s p. 246.
1 | 155 |  | 发电机功率 | 1000 | I32 | 719-720 | kw | Calculated active power on the generator and exponential averaged by Power Average Time x.xx s p. 246.
1 | 156 |  | 机组消耗功率 | 1000 | I32 | 721-722 | kw | Estimate of auxiliaries consumption to be compensated by the torque controller in Power Control Mode. See section 2.10.3 for details.
| 157 |  | 机械效率 | 1000 | I32 | 723-724 | / | Efficiency based on lookup table Mech. Efficiency Table p. 241

## 变频器
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 158 | Inverter | 变频器模式 | 1 | I16 | 800 | 字符串 | 1:"Reset" 2:"Stopped" 3:"Run" 4:"Grid Connected"
1 | 159 |  | 发电机转速（编码器） | 10 | I16 | 801 | rpm | Actual speed of the generator.
1 | 160 |  | 转矩 | 100 | I16 | 802 | % | Actual Generator torque in percentage
| 161 |  | 控制字 | 1 | I16 | 803 | /
1 | 162 |  | ON(bit 0) | 1 | I16 | 804 | 0/1
1 | 163 |  | RUN(bit 3) | 1 | I16 | 805 | 0/1
1 | 164 |  | RESET(bit 7） | 1 | I16 | 806 | 0/1
1 | 165 |  | 有功功率 | 10 | I16 | 807 | kW | Actual power.
1 | 166 |  | 无功功率 | 10 | I16 | 808 | kvar | Actual reactive power.
1 | 167 |  | 直流母线电压 | 10 | I16 | 809 | V | Mains voltage.
1 | 168 |  | 直流母线电流 | 10 | I16 | 810 | A | Line curreunt.
| 169 |  | 变频器PP温度 | 1 | I16 | 811 | °C | PP temperature in degrees centigrade.
| 170 |  | 变频器制动器 | 1 | I16 | 812 | 0/1 | Shows the status of the inverter brealer on 1.4#31 "Inverter Breaker" p. 545 (0 = Error, 1 = OK)
1 | 171 |  | 转矩变化率 | 100 | I16 | 813 | % | Torque setpoint used to control the inverter.
| 172 |  | 相角变化率 | 100 | I16 | 814 | °
| 284 | LVRT | LVRT上一次触发时间 | 1 | I64 | 1400-1403 | / | The time stamp of the last LVRT situation
| 285 |  | LVRT上一次持续时间 | 1 | I32 | 1404-1405 | ms | The duration time of the last LVRT situation

## 发电机
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
1 | 173 | Generator | 发电机转速（主控） | 100 | I32 | 900-901 | rpm | Generator rpm.
1 | 174 |  | 发电机转速1秒平均值 | 100 | I32 | 902-903 | rpm | Shows the 1 sec. averaged rotor speed
| 175 |  | 发电机转速30秒平均值 | 100 | I32 | 904-905 | rpm | Shows the 30 sec. averaged rotor speed
| 176 |  | 发电机转速10分钟平均值 | 100 | I32 | 906-907 | rpm | Shows the 600 sec. averaged rotor speed
| 177 |  | 发电机加热器模式 | 1 | I16 | 908 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 178 |  | 发电机滑环室加热模式 | 1 | I16 | 909 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 179 |  | 发电机风扇电机加热模式 | 1 | I16 | 910 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 180 |  | 发电机冷却模式 | 1 | I16 | 911 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
| 181 |  | 发电机滑环室冷却模式 | 1 | I16 | 912 | 字符串 | 1:"AUTO" 2:"BLOCKED" 3:"ON" 4:"OFF"
1 | 182 |  | 发电机频率 | 1000 | I32 | 913-914 | Hz | Shows the generator speed in Hz.
1 | 183 |  | 发电机L1绕组温度 | 10 | I16 | 915 | °C | Shows the (G) stator winding L1 temperature.
1 | 184 |  | 发电机L2绕组温度 | 10 | I16 | 916 | °C | Shows the (G) stator winding L2 temperature.
1 | 185 |  | 发电机L3绕组温度 | 10 | I16 | 917 | °C | Shows the (G) stator winding L3 temperature.
1 | 186 |  | 发电机驱动端轴承温度 | 10 | I16 | 918 | °C | Shows the (G) bearing DE temperature.
1 | 187 |  | 发电机非驱动端轴承温度 | 10 | I16 | 919 | °C | Shows the (G) bearing NDE temperature.
| 188 |  | 发电机加热器状态 | 1 | I16 | 920 | 0/1 | The current condition on output 3.2#14 "Heating Generator" p. 550 (0 = Heating OFF, 1 = Heating ON).
| 189 |  | 发电机滑环室加热器状态 | 1 | I16 | 921 | 0/1
| 190 |  | 发电机风扇加热器状态 | 1 | I16 | 922 | 0/1
| 191 |  | 发电机加热器反馈 | 1 | I16 | 923 | 0/1 | Heating feedback signal 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK).
| 192 |  | 发电机前置风扇反馈 | 1 | I16 | 924 | 0/1 | The current condition on output 3.2#16 "Generator Fan Front" p. 550 (0 = Fan OFF, 1 = Fan ON).
| 193 |  | 发电机顶部风扇反馈 | 1 | I16 | 925 | 0/1 | The current condition on output 3.2#17 "Generator Fan Top" p. 550 (0 = Fan OFF, 1 = Fan ON).
| 194 |  | 发电机滑环室风扇反馈 | 1 | I16 | 926 | 0/1
| 195 |  | 发电机风扇断路器反馈 | 1 | I16 | 927 | 0/1 | The current state of the fan feedback on 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK).
| 196 |  | 发电机碳刷报警 | 1 | I16 | 928 | 0/1 | The current state of the brush wear on 3.3#41 "Generator Brush Wear Error" p. 555 (0 = ERROR, 1 = OK).
1 | 197 |  | 发电机风扇出口温度 | 10 | I16 | 929 | °C | Shows the (G) fan outer temperature.
1 | 198 |  | 发电机滑环室温度 | 10 | I16 | 930 | °C
| 370 | Power Management | 功率控制模式 | 1 | I16 | 2900 | 字符串 | 1:"No Red. Active" 2:"Local, kW" 3:"Local, %" 4:"Remote" 5:"12345678901234567890" 6:"Freq. drop active" 7:"Grid: High Freq." 8:"Low Limit Active"
1 | 371 |  | 有功功率设定值 | 1000 | I32 | 2901-2902 | kW | Shows the requested active power production.
| 372 |  | 有功功率1秒平均值 | 1000 | I32 | 2903-2904 | kW | Active Power 1s xxxxx.x kW
| 373 |  | 有功功率10分钟平均值 | 1000 | I32 | 2905-2906 | kW | 10 minute average value of active power production.
| 374 |  | 无功功率设定值 | 1000 | I32 | 2907-2908 | kvar | Shows the requested reactive power.
| 375 |  | 无功功率1秒平均值 | 1000 | I32 | 2909-2910 | kvar | 1 second average value of reactive power production or consumption.
| 376 |  | 无功功率10分钟平均值 | 1000 | I32 | 2911-2912 | kvar | 10 minute average value of reactive power production or consumption.

## 主轴
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 60 | Brake Disk | 制动模式 | 1 | I16 | 400 | 字符串 | 1:"AUTO" 2:"MANUAL" 3:"UNKNOWN"
1 | 61 |  | 制动类型 | 1 | I16 | 401 | 字符串 | 1:"OPEN" 2:"CLOSE" 3:"AUTO CLOSE" 4:"UNKNOWN"
| 62 |  | 制动盘报警 | 1 | I16 | 402 | 0/1 | The current condition on input
| 63 |  | 液压制动松闸（0=抱闸/1=松闸） | 1 | I16 | 403 | 0/1 | The current condition on input
| 64 |  | 主轴制动释放 | 1 | I16 | 404 | 0/1 | 3.2-51#
| 65 |  | 主轴制动抱闸 | 1 | I16 | 405 | 0/1 | 3.2-52#
| 66 |  | 主轴转速设定值 | 100 | I32 | 500-501 | rpm | Speed setpoint from Operate to the PID controller.
1 | 199 | Rotor | 主轴转速 | 100 | I32 | 1000-1001 | rpm | Rotor rpm.
1 | 200 |  | 主轴轴承1温度 | 10 | I16 | 1002 | °C | The current temperature on PT100 input 3.3#69+ "Spindle Bearing 1" p. 620
1 | 201 |  | 主轴轴承2温度 | 10 | I16 | 1003 | °C | The current temperature on PT100 input 3.3#70+ "Spindle Bearing 2" p. 620
1 | 202 |  | 主轴软件超速 | 1 | I16 | 1004 | 0/1 | The current condition on input (0 = OK, 1 = Error).
1 | 203 |  | 液压站过滤器堵塞 | 1 | I16 | 1005 | 0/1 | The current condition on input 3.3#46 "Hydraulic Filter Blocked" p. 555 (1 = Error, 0 = OK). Used in status code 441 - Brake pressure p. 270
1 | 204 |  | 主轴刹车抱闸 | 1 | I16 | 1006 | 0/1 | The current condition on input 3.2#51 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 85 bar.
1 | 205 |  | 主轴刹车释放 | 1 | I16 | 1007 | 0/1 | The current condition on input 3.2#52 "" p. 552 (0 = Released, 1 = Locked). Indicates that the brake pressure is above 10 bar.
| 206 |  | 主轴锁定销1释放 | 1 | I16 | 1008 | 0/1 | The current condition on input 3.2#46 "Rotor Unlock 1" p. 551 (1 = Released, 0 = Locked).
| 207 |  | 主轴锁定销2释放 | 1 | I16 | 1009 | 0/1 | The current condition on input 3.2#47 "Rotor Unlock 2" p. 551 (1 = Released, 0 = Locked)
| 208 |  | 滑环加热器断路器反馈 | 1 | I16 | 1010 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0 = Error, 1 = OK).
1 | 209 |  | 主轴转速1秒平均值 | 100 | I32 | 1011-1012 | rpm | Shows the 1 sec. averaged rotor speed
| 210 |  | 主轴转速30秒平均值 | 100 | I32 | 1013-1014 | rpm | Shows the 30 sec. averaged rotor speed
| 211 |  | 主轴转速10分钟平均值 | 100 | I32 | 1015-1016 | rpm | Shows the 600 sec. averaged rotor speed
1 | 212 |  | 主轴频率 | 1000 | I32 | 1017-1018 | Hz | Shows the rotor frequency from the sensor

## 齿轮箱
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 213 | Gear | 齿轮箱润滑油过滤器压力反馈 | 1 | I16 | 1100 | 0/1 | The current gear oil filter pressure 3.3#43 "Gear Oil Presssure Status" p. 618.
| 214 |  | 齿轮箱过滤器堵塞 | 1 | I16 | 1101 | 0/1 | Filter clogged on 3.3#33 "Gear Box Filter Blooding" p. 618 (1 = clogged, 0 = OK).
| 215 |  | 齿轮箱润滑油油位 | 1 | I16 | 1102 | 0/1 | The current Gear oil level on 3.3#42 "Gear Oil Level/SNK" p. 555 (0=Err, 1=OK).
| 216 |  | 齿轮箱润滑油风扇 | 1 | I16 | 1103 | 0/1 | The current condition on output 3.3#8 "Gear Oil Cooling" p. 554 (0=Off, 1=On).
| 217 |  | 齿轮箱润滑油油泵和风扇断路器反馈 | 1 | I16 | 1104 | 0/1 | The current condition on output 3.3#26 "Feedback MCB Gear Box Oil Pump & Gear Oil Cooler" p. 555 (0=Err, 1=Ok).
| 218 |  | 齿轮箱润滑油加热器 | 1 | I16 | 1105 | 0/1 | The current condition on output 3.2#8 "Gear Oil Heating" p. 550 (0=Off, 1=On).
| 219 |  | 齿轮箱加热器反馈 | 1 | I16 | 1106 | 0/1 | The current condition on input 3.3#31 "Feedback Fuse Heaters" p. 555 (0=Err, 1=Ok).
| 220 |  | 齿轮箱润滑油泵高速 | 1 | I16 | 1107 | 0/1 | The current condition on output 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 (0=Off, 1=On).
| 221 |  | 齿轮箱润滑油泵低速 | 1 | I16 | 1108 | 0/1 | The current condition on output 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 (0=Off, 1=On).
| 222 |  | 齿轮箱风扇电机加热器 | 1 | I16 | 1109 | 0/1 | The current condition on output 3.3#10 "Gear Box Cooler Motor Heater" p. 554 (0=Off, 1=On). This output is set high if 3.3#8 "Gear Oil Cooling" p. 554 is 0.
| 223 |  | 齿轮箱油泵加热器 | 1 | I16 | 1110 | 0/1 | The current condition on output 3.2#19 "Gear Box Pump Heater" p. 551 (0=Off, 1=On). This output is set high if 3.3#5 "Gear Box Oil Pump (Low Speed)" p. 554 and 3.3#6 "Gear Box Oil Pump (High Speed)" p. 554 both are 0.
1 | 224 |  | 齿轮箱油温 | 10 | I16 | 1111 | °C | This parameter shows the actual measured temperature of the gear oil on on 3.3#65+ "Gear Box Oil Temp." p. 556.
1 | 225 |  | 齿轮箱油泵温度 | 10 | I16 | 1112 | °C | The current Gear pump oil temperature on 3.3#66+ "Gear Pump Oil Temp." p. 557.
1 | 226 |  | 齿轮箱轴承1温度 | 10 | I16 | 1113 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557.
1 | 227 |  | 齿轮箱轴承2温度 | 10 | I16 | 1114 | °C | The current Gear high speed bearing temperature on 3.3#67+ "Gear Box High Speed Bearing 1 Temp." p. 557.
1 | 228 |  | 齿轮箱进口油压 | 100 | I32 | 1115-1116 | bar | The current gear box import oil pressure on 3.2#64+ "Gear Box Import Oil Pressure" p. 552.
1 | 229 |  | 过滤器进口油压 | 100 | I32 | 1117-1118 | bar | The current filter import oil pressure on 3.2#63+ "Filter Import Oil Pressure" p. 552.

## 电网
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
1 | 230 | Grid | 电网电压 | 1 | I32 | 1200-1201 | V | The average of the three measured "Line to neutral"-voltages
1 | 231 |  | 电网电流 | 1 | I16 | 1202 | A | The average current for all three lines.
1 | 232 |  | 电网频率 | 1000 | I32 | 1203-1204 | Hz | The grid frequency measured by the grid module
1 | 233 |  | 电网有功功率 | 1000 | I32 | 1205-1206 | kW | The active power measured by the grid module
1 | 234 |  | 电网无功功率 | 1000 | I32 | 1207-1208 | kVAr | The reactive power measured by the grid module.
| 235 |  | 电网功率因数 | 1000 | I16 | 1209 | / | The power factor calculated by the grid module
1 | 236 |  | 电网L1相电压 | 1 | I32 | 1210-1211 | V | The L1 Voltage "Line to Neutral" measured by the grid module
1 | 237 |  | 电网L2相电压 | 1 | I32 | 1212-1213 | V | The L2 Voltage "Line to Neutral" measured by the grid module.
1 | 238 |  | 电网L3相电压 | 1 | I32 | 1214-1215 | V | The L3 Voltage "Line to Neutral" measured by the grid module.
1 | 239 |  | 电网L1相电流 | 1 | I16 | 1216 | A | The current on L1 measured by the grid module.
1 | 240 |  | 电网L2相电流 | 1 | I16 | 1217 | A | The current on L2 measured by the grid module.
1 | 241 |  | 电网L3相电流 | 1 | I16 | 1218 | A | The current on L3 measured by the grid module.
| 242 |  | 电网L1/L2相位角 | 1000 | I32 | 1219-1220 | ° | The phase angle between L1-L2.
| 243 |  | 电网L1/L3相位角 | 1000 | I32 | 1221-1222 | ° | The phase angle between L1-L3
| 244 |  | 有功功率100毫秒平均值 | 1000 | I32 | 1223-1224 | KW
| 245 |  | 有功功率1秒平均值 | 1000 | I32 | 1225-1226 | KW
| 246 |  | 有功功率3秒平均值 | 1000 | I32 | 1227-1228 | KW
| 247 |  | 有功功率30秒平均值 | 1000 | I32 | 1229-1230 | KW
| 248 |  | 有功功率10分钟平均值 | 1000 | I32 | 1231-1232 | KW
| 249 |  | 无功功率100毫秒平均值 | 1000 | I32 | 1233-1234 | kvar
| 250 |  | 无功功率1秒平均值 | 1000 | I32 | 1235-1236 | kvar
| 251 |  | 无功功率3秒平均值 | 1000 | I32 | 1237-1238 | kvar
| 252 |  | 无功功率30秒平均值 | 1000 | I32 | 1239-1240 | kvar
| 253 |  | 无功功率10分钟平均值 | 1000 | I32 | 1241-1242 | kvar
| 254 |  | L1相电压互感器变比 | 1000 | I32 | 1243-1244 | /
| 255 |  | L2相电压互感器变比 | 1000 | I32 | 1245-1246 | /
| 256 |  | L3相电压互感器变比 | 1000 | I32 | 1247-1248 | /
| 257 |  | L1相电流互感器变比 | 1000 | I32 | 1249-1250 | /
| 258 |  | L2相电流互感器变比 | 1000 | I32 | 1251-1252 | /
| 259 |  | L3相电流互感器变比 | 1000 | I32 | 1253-1254 | /
| 260 |  | 电网L1相峰值电压 | 1 | I32 | 1255-1256 | V | The highest voltage measured on L1 based on "Line to Neutral".
| 261 |  | 电网L1相峰值电压发生时间 | 1 | I64 | 1257-1260 | / | This menuline shows the timestamp for when the voltage peak, see Peak Volt. L1 x V p. 332, occured.
| 262 |  | 电网L2相峰值电压 | 1 | I32 | 1261-1262 | V | The highest voltage measured on L2 based on "Line to Neutral".
| 263 |  | 电网L2相峰值电压发生时间 | 1 | I64 | 1263-1266 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L2 x V p. 332, occured.
| 264 |  | 电网L3相峰值电压 | 1 | I32 | 1267-1268 | V | The highest voltage measured on L3 based on "Line to Neutral".
| 265 |  | 电网L3相峰值电压发生时间 | 1 | I64 | 1269-1272 | / | This menuline shows the time stamp for when the voltage peak, see Peak Volt. L3 x V p. 332, occured.
| 266 |  | 电网L1相峰值电流 | 1 | I32 | 1273-1274 | A | The highest current measured on L1
| 267 |  | 电网L1相峰值电流发生时间 | 1 | I64 | 1275-1278 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L1 x A p. 332, occured.
| 268 |  | 电网L2相峰值电流 | 1 | I32 | 1279-1280 | A | The highest current measured on L2.
| 269 |  | 电网L2相峰值电流发生时间 | 1 | I64 | 1281-1284 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L2 x A p. 333, occured.
| 270 |  | 电网L3相峰值电流 | 1 | I32 | 1285-1286 | A | The highest current measured on L3
| 271 |  | 电网L3相峰值电流发生时间 | 1 | I64 | 1287-1290 | / | This menuline shows the time stamp for when the voltage peak, see Peak Cur. L3 x A p. 333, occured.
| 272 |  | 电网L1相最大正向矢量波动值 | 1000 | I32 | 1291-1292 | ° | The highest positive peak vector surge on L1.
| 273 |  | 电网L1相最大正向矢量波动值发生时间 | 1 | I64 | 1293-1296 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L1 x.x ° p. 333, has occured.
| 274 |  | 电网L2相最大正向矢量波动值 | 1000 | I32 | 1297-1298 | ° | The highest positive peak vector surge on L2.
| 275 |  | 电网L2相最大正向矢量波动值发生时间 | 1 | I64 | 1299-1302 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L2 x.x ° p. 333, has occured.
| 276 |  | 电网L3相最大正向矢量波动值 | 1000 | I32 | 1303-1304 | ° | The highest positive peak vector surge on L3
| 277 |  | 电网L3相最大正向矢量波动值发生时间 | 1 | I64 | 1305-1308 | / | This menuline shows the timestamp for when the peak value for vector surge in positive direction, see Peak Vec. Sur. Pos. L3 x.x ° p. 334, has occured
| 278 |  | 电网L1相最大负向矢量波动值 | 1000 | I32 | 1309-1310 | ° | The highest negative peak vector surge on L1
| 279 |  | 电网L1相最大负向矢量波动值发生时间 | 1 | I64 | 1311-1314 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L1 x.x ° p. 334, has occured.
| 280 |  | 电网L2相最大负向矢量波动值 | 1000 | I32 | 1315-1316 | ° | The highest negative peak vector surge on L2
| 281 |  | 电网L2相最大负向矢量波动值发生时间 | 1 | I64 | 1317-1320 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L2 x.x ° p. 334, has occured.
| 282 |  | 电网L3相最大负向矢量波动值 | 1000 | I32 | 1321-1322 | ° | The highest negative peak vector surge on L3.
| 283 |  | 电网L3相最大负向矢量波动值发生时间 | 1 | I64 | 1323-1326 | / | This menuline shows the timestamp for when the peak value for vector surge in negative direction, see Peak Vec. Sur. Neg. L3 x.x ° p. 334, has occured.

## 液压站
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 286 | Hydraulic | 液压站状态 | 1 | I16 | 1500 | 字符串 | 1:"Blocked" 2:"Service On" 3:"Service Off" 4:"Auto"
| 287 |  | 液压站油泵状态 | 1 | I16 | 1501 | 0/1 | The current condition on 3.2#7 "Hydraulic pump" p. 550 (0 = Off, 1 = On).
| 288 |  | 液压站油泵过载（0=Error/1=OK） | 1 | I16 | 1502 | 0/1 | The current condition on input 3.3#27 "Feedback MCB" p. 555 (0 = Error, 1 = OK).
| 289 |  | 液压站油位 | 1 | I16 | 1503 | 0/1 | The current condition on input 3.3#38 "Hydraulic Oil Level" p. 555 (0 = Low, 1 = OK).
| 290 |  | 液压站温度高（>70） | 1 | I16 | 1504 | 0/1 | The current condition on input 3.3#28 "Hydraulic Temp. High (>=70 °C)" p. 555 (0 = OK, 1 = High).
| 291 |  | 液压站系统压力（1=OK/0=Low） | 1 | I16 | 1505 | 0/1 | The current pressure condition on input 3.3#44 "Hydraulic System Pressure Motor Start (Position 40)" p. 555 (1 = OK, 0 = Low).
| 292 |  | 液压站系统压力（1=OK/0=High） | 1 | I16 | 1506 | 0/1 | The current pressure condition on input 3.3#45 "" p. 555 (1 = OK, 0 = High).
1 | 293 |  | 液压站压力 | 100 | I32 | 1507-1508 | bar | The current condition on the scaled input 3.2#62+ "Hydraulic Pressure" p. 552 (in bar).

## 反馈点error
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
294 | PT100 | 反馈点1.4.65信号错误 | 1 | I16 | 1600 | 0/1
295 |  | 反馈点1.4.66信号错误 | 1 | I16 | 1601 | 0/1
296 |  | 反馈点1.4.67信号错误 | 1 | I16 | 1602 | 0/1
297 |  | 反馈点1.4.68信号错误 | 1 | I16 | 1603 | 0/1
298 |  | 反馈点1.4.69信号错误 | 1 | I16 | 1604 | 0/1
299 |  | 反馈点3.2.65信号错误 | 1 | I16 | 1605 | 0/1
300 |  | 反馈点3.2.66信号错误 | 1 | I16 | 1606 | 0/1
301 |  | 反馈点3.2.67信号错误 | 1 | I16 | 1607 | 0/1
302 |  | 反馈点3.2.68信号错误 | 1 | I16 | 1608 | 0/1
303 |  | 反馈点3.2.69信号错误 | 1 | I16 | 1609 | 0/1
304 |  | 反馈点3.2.70信号错误 | 1 | I16 | 1610 | 0/1
305 |  | 反馈点3.2.71信号错误 | 1 | I16 | 1611 | 0/1
306 |  | 反馈点3.2.72信号错误 | 1 | I16 | 1612 | 0/1
307 |  | 反馈点3.3.65信号错误 | 1 | I16 | 1613 | 0/1
308 |  | 反馈点3.3.66信号错误 | 1 | I16 | 1614 | 0/1
309 |  | 反馈点3.3.67信号错误 | 1 | I16 | 1615 | 0/1
310 |  | 反馈点3.3.68信号错误 | 1 | I16 | 1616 | 0/1
311 |  | 反馈点3.3.69信号错误 | 1 | I16 | 1617 | 0/1
312 |  | 反馈点3.3.70信号错误 | 1 | I16 | 1618 | 0/1
313 |  | 反馈点3.3.72信号错误 | 1 | I16 | 1619 | 0/1
314 | 4-20mA | 反馈点3.2.62信号错误 | 1 | I16 | 1700 | 0/1
315 |  | 反馈点3.2.63信号错误 | 1 | I16 | 1701 | 0/1
316 |  | 反馈点3.3.61信号错误 | 1 | I16 | 1702 | 0/1
317 |  | 反馈点3.3.62信号错误 | 1 | I16 | 1703 | 0/1

## 测风仪
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
318 | Anemometer | 3秒平均风速 | 100 | I16 | 1800 | m/s | This shows the 3 sec. averaged wind speed. | V_WindSpeed3Sec
319 |  | 30秒平均风速 | 100 | I16 | 1801 | m/s | This shows the 30 sec. averaged wind speed | V_WindSpeed30Sec
319+ |  | 10分钟平均风速 | 100 | I16 | 1802 | m/s |  | V_WindSpeed10Min
320 |  | 当前使用的风速仪 | 1 | I16 | 1803 | / | This parameter shows the active anemometer. | V_WindSpeedActive
321 |  | 风速 | 100 | I16 | 1804 | m/s | This parameter shows the wind speed from the selected anemometer. | AI_WindSpeed
322 |  | 风速仪1实际反馈值 | 1000 | I32 | 1805-1806 | Hz |  | HSI_WindSpeedOne_Frq
323 |  | 风速仪2实际反馈值 | 1000 | I32 | 1807-1808 | Hz |  | HSI_WindSpeedTwo_Frq
324 | Wind Vane | 3秒平均风向 | 10 | I16 | 1900 | ° | Shows the 3 seconds averaged wind direction from the selected windvane. | V_WindVaneDirection3Sec
325 |  | 30秒平均风向 | 10 | I16 | 1901 | ° | Shows the 30 seconds averaged wind direction from the selected wind vane | V_WindVaneDirection30Sec
325+ |  | 10分钟平均风速 | 10 | I16 | 1092 | ° |  | V_WindDirection10M
326 |  | 风向 | 10 | I16 | 1903 | ° | Shows the wind direction from the active wind vane. | AI_WindVaneDirection
327 |  | 机舱相对风向偏移量 | 10 | I16 | 1904 | ° | Shows how many degrees the nacelle is out of the wind. The value goes from -179°to 0°to 180°, where 0°is when the nacelle is aligned according to the correct wind direction. | V_RelaWindVaneDirection3Sec
328 |  | 机舱相对正北角度 | 10 | I16 | 1905 | ° | Shows the position of the nacelle seen in proportion to a circle where 0°is North. | V_NacelleDirection
329 |  | 当前使用的风向仪 | 1 | I32 | 1906-1907 | / | Shows which of the two wind vanes is currently active | V_WindVaneActiveVane
330 |  | 风向仪1相对正北角度 | 10 | I16 | 1908 | ° | Shows the wind direction seen in proportion to a circle where 0°is North. | V_WindDirection1
331 |  | 风向仪2相对正北角度 | 10 | I16 | 1909 | ° | Shows the wind direction 2 seen in proportion to a circle where 0°is North. | V_WindDirection2
332 |  | 风向仪1相对机舱角度 | 10 | I16 | 1910 | ° | Shows the wind vane 1 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection1
333 |  | 风向仪2相对机舱角度 | 10 | I16 | 1911 | ° | Shows the wind vane 2 direction seen in proportion to a circle where 0°is the nacelle direction. | AI_WindVaneDirection2
334 |  | 风向仪1实际反馈值 | 1000 | I16 | 1912 | mA |  | AI_WindDirection1Current
335 |  | 风向仪2实际反馈值 | 1000 | I16 | 1913 | mA |  | AI_WindDirection2Current
336 | Outdoor | 测风仪加热器状态 | 1 | I16 | 2000 | 0/1 | The current condition on output 3.2#15 "Heating wind sensor" p. 550 (0 = Off, 1 = On). | DO_HeatingWindSensor
337 |  | 环境温度 | 10 | I16 | 2001 | °C | The measured environment temperature on input 1.4#69+ "Enviroment Temperature" p. 547. | PT_OutdoorTemp

## 塔基
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
1 | 337 |  | 环境温度 | 10 | I16 | 2001 | °C | The measured environment temperature on input 1.4#69+ "Enviroment Temperature" p. 547.
| 338 | Lightning | 塔基柜内浪涌保护器 | 1 | I16 | 2100 | 0/1 | The current state of input 1.4#29 "Surge Protection (Tower Base)" p. 545.
| 340 | Transformer | 箱变温度1 | 10 | I16 | 2200 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546).
| 341 |  | 箱变温度2 | 10 | I16 | 2201 | °C | Transformer temperature. PT100 temperature sensor (Terminal 1.4#68+ "Transfomer Temp. 2" p. 547).
| 342 |  | 35KV开关状态（0=OFF/1=ON） | 1 | I16 | 2202 | 0/1 | Shows the status of the 35 kV switch (Terminal 1.4#33 "Measuring open/close of the 35 kV switch" p. 545, 0 = OFF, 1 = ON).
| 343 |  | 690V开关状态（0=OFF/1=ON） | 1 | I16 | 2203 | 0/1 | Shows the status of the 690 volt switch (Terminal 1.4#34 "Measuring open/close of the 0.69 kV switch" p. 545, 0 = OFF, 1 = ON).
| 344 |  | 箱变温度高 | 1 | I16 | 2204 | 0/1
| 345 |  | 箱变油位状态 | 1 | I16 | 2205 | 0/1
1 | 350 | Tower Base | 塔基温度 | 10 | I16 | 2400 | °C | Tower base temperature (Terminal 1.4#67+ "Transfomer Temp. 1" p. 546)
| 351 |  | 塔基烟雾报警 | 1 | I16 | 2401 | 0/1
| 352 | Ups | UPS通讯OK | 1 | I16 | 2500 | 0/1 | Communication status
| 353 |  | UPS剩余时间 | 1 | I32 | 2501-2502 | s | The measured UPS remaining operation time with nominel load. The value is received through the serial connection to the UPS. In case of any communication error, the UPS remaining time is forced to zero.

## 机舱
| 序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  |  | 倍数 | 数据类型 | 地址
| 339 |  | 机舱柜内浪涌保护器 | 1 | I16 | 2101 | 0/1 | The current state of input 3.3#50 "Surge Protection Nacelle" p. 555.
| 346 | Air Pressure | 当前大气压力 | 1 | I16 | 2300 | mbar
| 347 |  | 1秒平均气压 | 1 | I16 | 2301 | mbar
| 348 |  | 30秒平均气压 | 1 | I16 | 2302 | mbar
| 349 |  | 10分钟平均气压 | 1 | I16 | 2303 | mbar
1 | 377 | Vibration monitoring | 振动传感器1通道1值 | 1000 | I16 | 3000 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1
1 | 378 |  | 振动传感器1通道2值 | 1000 | I16 | 3001 | G | Shows the vibration level in sensor WP4084 No. 1, channel 2
| 379 |  | 振动传感器1通道1+2值 | 1000 | I16 | 3002 | G | Shows the vibration level in sensor WP4084 No. 1, channel 1 + channel 2
| 380 |  | 振动传感器1通道1状态 | 1 | I16 | 3003 | 0/1 | Shows the status of the WP4084 No. 1, channel 1 (0 = Ok, 1 = Vibration alarm, 2 = Selftest error). See section 2.39.5 for further details on sensor monitoring.
| 381 |  | 振动传感器1通道2状态 | 1 | I16 | 3004 | 0/1 | Shows the status of the sensor selftest (0 = Idle, 1 = Active). See section 2.39.4 for further details on sensor selftest.
| 382 |  | 软件自检类型 | 1 | I16 | 3005 | 0/1 | Shows the selftest failure delay used by the sensor selftest software. (0 = 24 hours, 1 = 24 minutes). See section 2.39.4 for further details on sensor selftest.
| 383 |  | 振动传感器1通讯状态 | 1 | I16 | 3006 | 字符串 | 1:"Disabled" 2:"Error" 3:"Ok"
| 384 | Flight Warning Light | 航空灯供电OK | 1 | I16 | 3100 | 0/1 | The current condition on input 3.3#36 "Supply Obstruction Lights 1 & 2 230V" p. 555 (0 = Error, 1 = Ok).
| 385 |  | 航空灯故障 | 1 | I16 | 3101 | 0/1 | The current condition on input 3.3#37 "Flight Warning Error" p. 555 (1 = Error, 0 = Ok).
1 | 354 | Lubrication | 发电机润滑油泵状态 | 1 | I16 | 2600 | 0/1
1 | 355 |  | 轮毂轴承润滑油油位 | 1 | I16 | 2601 | 0/1 | The current condition on input 3.3#39 "Pitch Bearing Inner Ring Lubrication Grease Level" p. 555 (0 = Empty, 1 = OK).
1 | 356 |  | 轮毂轴承润滑油堵塞 | 1 | I16 | 2602 | 0/1 | The current condition on input 3.3#40 "Pitch Bearing Inner Ring Lubrication Blinding" p. 555 (Pulsing = OK, Not pulsing = Err).
1 | 357 |  | 轮毂润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2603 | 0/1 | The current condition on output 3.2#20 "Lubrication Pump Pitch System (Outer Ring)" p. 551 (0 = OFF, 1 = ON).
1 | 358 |  | 机舱轴承润滑油油位 | 1 | I16 | 2604 | 0/1
1 | 359 |  | 机舱轴承润滑油堵塞 | 1 | I16 | 2605 | 0/1 | The current condition on input 3.2#43 "Yaw Bear Lubrication Blinding" p. 551 (Pulsing = OK, Not pulsing = Err)
1 | 360 |  | 机舱润滑油泵状态（0=OFF/1=ON） | 1 | I16 | 2606 | 0/1 | The current condition on output 3.3#9 "Yaw Lubrication Pump 1" p. 554 (0 = OFF, 1 = ON).
1 | 361 | Nacelle | 机舱温度 | 10 | I16 | 2700 | °C | Nacelle temperature on PT100 input 3.2#65+ "Nacelle Temperature" p. 553.
| 362 |  | 机舱风扇状态 | 1 | I16 | 2701 | 0/1 | Nacelle fan ON/OFF (output 3.2#18 "Nacelle Fan 1 & 2" p. 550).
| 363 |  | 机舱风扇断路器反馈 | 1 | I16 | 2702 | 0/1 | Nacelle fan MCB FB ON/OFF (input 3.3#27 "Feedback MCB" p. 555).
| 364 |  | 机舱加热器1+2状态 | 1 | I16 | 2703 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF"
| 365 |  | 机舱加热器3+4状态 | 1 | I16 | 2704 | 字符串 | 1:"BLOCKED" 2:"AUTO ON" 3:"AUTO OFF" 4:"FORCED ON" 5:"FORCED OFF"
| 366 |  | 机舱烟雾报警 | 1 | I16 | 2705 | 0/1
1 | 367 | Panels | 机舱柜温度 | 10 | I16 | 2800 | °C | Shows the status of the nacelle control panel temperature (Terminal 3.2#66+ "Nacelle Panel Temperature" p. 553).
1 | 368 |  | 塔基柜温度 | 10 | I16 | 2801 | °C | Shows the temperature of the tower base panel (Terminal 1.4#65+ "Tower Base Panel Temperature" p. 546).
| 369 |  | 以太网开关OK | 1 | I16 | 2802 | 0/1 | Shows the status of the ethernet switch ES100 (Terminal 1.4#32 "Ethernet Switch ES100 OK" p. 545)

## 统计
序号 | 目录 | 名称 | Config |  |  | 单位 | 描述
|  |  | 倍数 | 数据类型 | 地址
393 | 机组部件运行统计 | 顺时针偏航激活时长 | 10 | I64 | 3300-3303 | 小时 | DO_YawMotorCw
394 |  | 顺时针偏航激活次数 | 1 | I64 | 3304-3307 | 次
395 |  | 逆时针偏航激活时长 | 10 | I64 | 3308-3311 | 小时 | DO_YawMotorCcw
396 |  | 逆时针偏航激活次数 | 1 | I64 | 3312-3315 | 次
397 |  | 偏航电机激活时长 | 10 | I64 | 3316-3319 | 小时 | V_SumYawMotorActive
398 |  | 偏航电机激活次数 | 1 | I64 | 3320-3323 | 次
399 |  | 刹车盘抱闸时长 | 10 | I64 | 3324-3327 | 小时 | V_SumBrakeDisk
400 |  | 刹车盘抱闸次数 | 1 | I64 | 3328-3331 | 次
401 |  | 刹车盘施放时长 | 10 | I64 | 3332-3335 | 小时 | V_SumBrakeFree
402 |  | 刹车盘释放次数 | 1 | I64 | 3336-3339 | 次
403 |  | 发电机加热器工作时长 | 10 | I64 | 3340-3343 | 小时 | DO_GeneratorHeating
404 |  | 发电机加热器工作次数 | 1 | I64 | 3344-3347 | 次
405 |  | 发电机滑环室加热器工作时长 | 10 | I64 | 3348-3351 | 小时 | DO_GeneratorSRHeater
406 |  | 发电机滑环室加热器工作次数 | 1 | I64 | 3352-3355 | 次
407 |  | 发电机风扇电机加热器工作时长 | 10 | I64 | 3356-3359 | 小时 | DO_GeneratorFansHeater
408 |  | 发电机风扇电机加热器工作次数 | 1 | I64 | 3360-3363 | 次
409 |  | 发电机滑环室风扇工作时长 | 10 | I64 | 3364-3367 | 小时 | DO_GeneratorSRFans
410 |  | 发电机滑环室风扇工作次数 | 1 | I64 | 3368-3371 | 次
411 |  | 发电机风扇1工作时长 | 10 | I64 | 3372-3375 | 小时 | DO_GeneratorFanFront
412 |  | 发电机风扇1工作次数 | 1 | I64 | 3376-3379 | 次
413 |  | 发电机风扇2工作时长 | 10 | I64 | 3380-3383 | 小时 | DO_GeneratorFanTop
414 |  | 发电机风扇2工作次数 | 1 | I64 | 3384-3387 | 次
415 |  | 齿轮箱润滑油加热器工作时长 | 10 | I64 | 3388-3391 | 小时 | DO_GearOilHeating
416 |  | 齿轮箱润滑油加热器工作次数 | 1 | I64 | 3392-3395 | 次
417 |  | 齿轮箱风扇工作时长 | 10 | I64 | 3396-3399 | 小时 | DO_GearOilCoolerHighSpeed
418 |  | 齿轮箱风扇工作次数 | 1 | I64 | 3400-3403 | 次
419 |  | 齿轮箱油泵低速工作时长 | 10 | I64 | 3404-3407 | 小时 | DO_GearBoxOilPumpLowSpeed
420 |  | 齿轮箱油泵低速工作次数 | 1 | I64 | 3408-3411 | 次
421 |  | 齿轮箱油泵高速工作时长 | 10 | I64 | 3412-3415 | 小时 | DO_GearBoxOilPumpHighSpeed
422 |  | 齿轮箱油泵高速工作次数 | 1 | I64 | 3416-3419 | 次
423 |  | 液压站油泵工作时长 | 10 | I64 | 3420-3423 | 小时 | DO_HydraulicPump
424 |  | 液压站油泵工作次数 | 1 | I64 | 3424-3427 | 次
425 |  | 测风仪加热器工作时长 | 10 | I64 | 3428-3431 | 小时 | DO_HeatingWindSensor
426 |  | 测风仪加热器工作次数 | 1 | I64 | 3432-3435 | 次
| 电量统计 | 总发电量 | 1 | I64 | 3500-3503 | kWh | S_TotalProduction
|  | 总用电量 | 1 | I64 | 3504-3507 | kWh
|  | 日发电量 | 1 | I64 | 3508-3511 | kWh
|  | 日用电量 | 1 | I64 | 3512-3515 | kWh
|  | 周发电量 | 1 | I64 | 3516-3519 | kWh
|  | 周用电量 | 1 | I64 | 3520-3523 | kWh
|  | 月发电量 | 1 | I64 | 3524-3527 | kWh
|  | 月用电量 | 1 | I64 | 3528-3531 | kWh
|  | 年发电量 | 1 | I64 | 3532-3535 | kWh
|  | 年用电量 | 1 | I64 | 3536-3539 | kWh
| 时间统计 | 总发电时间 | 10 | I64 | 3540-3543 | 小时 | S_TotalOperation
|  | 日发电时间 | 10 | I64 | 3544-3547 | 小时
|  | 周发电时间 | 10 | I64 | 3548-3551 | 小时
|  | 月发电时间 | 10 | I64 | 3552-3555 | 小时
|  | 年发电时间 | 10 | I64 | 3556-3559 | 小时
|  | 总运行时间 | 10 | I64 | 3560-3563 | 小时 | S_Operate
|  | 日运行时间 | 10 | I64 | 3564-3567 | 小时
|  | 周运行时间 | 10 | I64 | 3568-3571 | 小时
|  | 月运行时间 | 10 | I64 | 3572-3575 | 小时
|  | 年运行时间 | 10 | I64 | 3576-3579 | 小时
|  | 总停机时间 | 10 | I64 | 3580-3583 | 小时 | S_OperationStopped
|  | 日停机时间 | 10 | I64 | 3584-3587 | 小时
|  | 周停机时间 | 10 | I64 | 3588-3591 | 小时
|  | 月停机时间 | 10 | I64 | 3592-3595 | 小时
|  | 年停机时间 | 10 | I64 | 3596-3599 | 小时
|  | 总启动风速时间 | 10 | I64 | 3600-3603 | 小时 | S_Startwind
|  | 日启动风速时间 | 10 | I64 | 3604-3607 | 小时
|  | 周启动风速时间 | 10 | I64 | 3608-3611 | 小时
|  | 月启动风速时间 | 10 | I64 | 3612-3615 | 小时
|  | 年启动风速时间 | 10 | I64 | 3616-3619 | 小时
| 风速统计 | 总平均风速 | 10 | I32 | 3620-3621 | m/s | S_WindspeedAvg
|  | 日平均风速 | 10 | I32 | 3622-3623 | m/s
|  | 周平均风速 | 10 | I32 | 3624-3625 | m/s
|  | 月平均风速 | 10 | I32 | 3626-3627 | m/s
|  | 年平均风速 | 10 | I32 | 3628-3629 | m/s
| 可利用率统计 | 总可利用率 | 100 | F32 | 3630-3631 | % | Availability
|  | 日可利用率 | 100 | F32 | 3632-3633 | %
|  | 周可利用率 | 100 | F32 | 3634-3635 | %
|  | 月可利用率 | 100 | F32 | 3636-3637 | %
|  | 年可利用率 | 100 | F32 | 3638-3639 | %

## 日报
日期 |  | 风电场名称-报表名称
风机编号 | 总发电量 (kWh) | 总发电时间 (h) | 日发电量 (kWh) | 日用电量 （kwh) | 日运行时间 (h) | 日故障时间 (h) | 日大于启动风速时间 (h) | 日发电时间 (h) | 日平均风速 (m/s) | 故障代码 | 备注(故障描述)
1# | 3500-3503 | 3540-3543 | 3508-3511 | 3512-3515 | 3564-3567 | 3584-3587 | 3604-3607 | 3544-3547 | 3630-3631 | 手填 | 手填
| I64 | I64 | I64 | I64 | I64 | I64 | I64 | I64 | I64
合计 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 周报
日期 |  | 风电场名称-报表名称
机组编号 | 周平均风速 （m/s） | 周发电量 （kWh） | 周发电时间 （h） | 周可利用率 （%） | 周可利用率修正 （%） | 可利用率修正原因说明
1# | 3636-3637 | 3516-3519 | 3548-3551 | 3654-3655 | 手填 | 手填
| I32 | I64 | I64 | F32
合计 |  | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 月报
日期 |  | 风电场名称-报表名称
机组编号 | 月平均风速 (m/s) | 月平均环境温度 (℃) | 月发电量 (kWh) | 月用电量 (kWh) | 月发电时间 (h) | 月停机时间 (h) | 月等效利用小时数 (h) | 月可利用率 （%） | 年发电量 (kWh) | 总发电量 (kWh) | 总发电时间 (h) | 总运行时间 (h) | 因电网或业主自身原因 |  |  | 因合同中约定机组故障原因
[13 empty] | 停机时间 (h) | 修正可利用率 （%） | 可利用率修正原因 （如有修正必须注明） | 停机时间 (h) | 修正可利用率 （%） | 可利用率修正原因 （如有修正必须注明）
1# | 3626-3627 | 由SCADA计算 | 3524-3527 | 3528-3531 | 3552-3555 | 3592-3595 | 由SCADA计算 | 3636-3637 | 3532-3535 | 3500-3503 | 3540-3543 | 3560-3563 | 手填 | 手填 | 手填 | 手填 | 手填 | 手填
| I32 | I16 | I64 | I64 | I64 | I64 |  | F32 | I64 | I64 | I64 | I64
合计 |  |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 年报
日期 |  |  | 风电场名称-报表名称
机组编号 | 年平均风速 （m/s） | 年平均环境温度 (℃) | 年发电量 （kW） | 年用电量 (kWh) | 年发电时间 （h） | 年停机时间 (h) | 年等效利用小时数 (h) | 年可利用率 （%） | 总发电量 (kWh) | 总发电时间 (h) | 总运行时间 (h)
1# | 3628-3629 | 由SCADA计算 | 3532-3535 | 3536-3539 | 3556-3559 | 3596-3599 | 由SCADA计算 | 3638-3639 | 3500-3503 | 3540-3543 | 3560-3563
| I32 |  | I64 | I64 | I64 | I64 |  | F32 | I64 | I64 | I64
合计 |  |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 |  | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 性能指标
日期
机组编号 | 风速 （m/s） | 有功功率 （kw） | 无功功率 （kvar） | 发电机L1绕组温度 (°C) | 发电机L2绕组温度 (°C) | 发电机L3绕组温度 (°C) | 发电机驱动端轴承温度 (°C) | 发电机非驱动端轴承温度 (°C) | 发电机风扇出口温度 (°C) | 发电机滑环室温度 (°C) | 主轴转速 （rpm） | 主轴轴承1温度 (°C) | 主轴轴承2温度 (°C) | 齿轮箱油温 (°C) | 齿轮箱油泵温度 (°C) | 齿轮箱轴承1温度 (°C) | 齿轮箱轴承2温度 (°C) | 齿轮箱进口油压 (bar) | 过滤器进口油压 (bar) | 液压站压力 (bar) | 塔基温度 | 环境温度
1# | 1800 | 807 | 808 | 915 | 916 | 917 | 918 | 919 | 929 | 930 | 1000-1001 | 1002 | 1003 | 1111 | 1112 | 1113 | 1114 | 1115-1116 | 1117-1118 | 1507-1508 | 2400 | 2001
| I16 | I16 | I16 | I16 | I16 | I16 | I16 | I16 | I16 | I16 | I32 | I16 | I16 | I16 | I16 | I16 | I16 | I32 | I32 | I32 | I16 | I16
平均值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最大值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算
最小值 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算 | 由SCADA计算

## 故障代码表
机组故障代码表
故障代码 | 故障名称 | 地址 | 故障分类 | 故障级别 | 英文名称 | 报警:B0 | 一般故障停机:B50 | 快速停机:B99 | 紧急停机:B199/B200
0 | 系统正常 | 5000 | 主控 | 报警 | System OK
5 | 振动故障 | 5010 | 机舱 | 紧急停机 | Vibration
7 | 机组处于维护模式 | 5020 | 主控 | 报警 | Turbine is serviced
10 | 安全链断开 | 5030 | 安全链 | 紧急停机 | Safety Chain Open
13 | 手动停机 | 5040 | 主控 | 一般故障停机 | Manual Stop
23 | 重复故障 | 5050 | 主控 | 一般故障停机 | Repeating error
30 | 机舱温度报警 | 5060 | 机舱 | 报警 | Nacelle Temp.
31 | 机舱温度停机 | 5070 | 机舱 | 一般故障停机 | Nacelle Temp. Stop
32 | 控制柜温度过高 | 5080 | 主控 | 一般故障停机 | High Temp.Cont.Panel
33 | 控制柜温度过低 | 5090 | 主控 | 一般故障停机 | Low Temp.Cont.Panel
41 | UPS电池电量低 | 5100 | 主控 | 快速停机 | UPS Battery Low
45 | 主控模块电源电压低 | 5110 | 主控 | 快速停机 | Main ctrl.Supply
55 | 主控模块手动重启 | 5120 | 主控 | 一般故障停机 | Main ctrl.man.reboot
92 | 机舱紧急停机 | 5130 | 机舱 | 紧急停机 | Emer.Stop Nacelle
100 | 重复电网故障 | 5140 | 电网 | 快速停机 | Repeated grid error
103 | 电网电压矢量浪涌 | 5150 | 电网 | 紧急停机 | Vector surge
110 | 电压高于等级1 | 5160 | 电网 | 快速停机 | Voltage high
111 | 电压低于等级1 | 5170 | 电网 | 快速停机 | Voltage low
113 | 箱变温度1高报警 | 5180 | 箱变 | 一般故障停机 | Trafo overtemp.
114 | 箱变温度2高停机 | 5190 | 箱变 | 一般故障停机 | Trafo temp. stop
115 | 电压低于等级2 | 5200 | 电网 | 快速停机 | Voltage low level 2
116 | 电压高于等级2 | 5210 | 电网 | 快速停机 | Voltage high level 2
120 | 频率过高 | 5220 | 电网 | 快速停机 | Frequency high
121 | 频率过低 | 5230 | 电网 | 快速停机 | Frequency low
130 | L1-L2-L3相角过大 | 5240 | 电网 | 快速停机 | L1-L2-L3 120°
170 | 电网故障无法启动 | 5250 | 电网 | 一般故障停机 | Grid <> Start Cond.
173 | 频率过高2 | 5260 | 电网 | 快速停机 | Frequency high 2
174 | 频率过低2 | 5270 | 电网 | 快速停机 | Frequency low 2
200 | 室外温度过低 | 5280 | 主控 | 报警 | Outdoor Temp. Low
201 | 室外温度过高 | 5290 | 主控 | 一般故障停机 | Outdoor Temp. High
202 | 风速小于功率 | 5300 | 机舱 | 一般故障停机 | Wind < power
203 | 风速大于功率 | 5310 | 机舱 | 一般故障停机 | Wind > power
205 | 塔基共振时间过长 | 5320 | 主控 | 一般故障停机 | Tower resonance time
210 | 测风仪结冰 | 5330 | 机舱 | 一般故障停机 | Anemom. iced over
220 | 两风速仪测量值偏差过大 | 5340 | 机舱 | 一般故障停机 | W.Speed Nonidentical
221 | 两风向仪测量值偏差过大 | 5350 | 机舱 | 一般故障停机 | W.Direc. Nonidentical
226 | 风测量故障 | 5360 | 机舱 | 一般故障停机 | Wind gauge defect
230 | 风速仪1故障 | 5370 | 机舱 | 报警 | Anemometer 1 defect
231 | 风速仪2故障 | 5380 | 机舱 | 报警 | Anemometer 2 defect
233 | 风速小于启动风速 | 5390 | 机舱 | 报警 | Wind < start cond.
234 | 风速小于偏航风速 | 5400 | 机舱 | 报警 | Wind < yaw cond.
235 | 风向仪故障 | 5410 | 机舱 | 一般故障停机 | Windvanes Defect
236 | 室外温度过低停机 | 5420 | 主控 | 一般故障停机 | Outdoor Temp.LowStp
237 | 室外温度过高停机 | 5430 | 主控 | 一般故障停机 | Outdoor Temp.Hi. Stp
250 | 风速过大 | 5440 | 机舱 | 一般故障停机 | Wind > max
251 | 风速太大 | 5450 | 机舱 | 一般故障停机 | Wind > maxmax
260 | 风向仪1故障 | 5460 | 机舱 | 报警 | Windvane 1 Defect
261 | 风向仪2故障 | 5470 | 机舱 | 报警 | Windvane 2 Defect
270 | 风向仪结冰 | 5480 | 机舱 | 一般故障停机 | Windvane Iced Over
300 | 发电机转速不匹配 | 5490 | 发电机 | 快速停机 | (G) Tacho Defect
302 | 主轴转速不匹配 | 5500 | 主轴 | 快速停机 | (R) Tacho Defect
311 | 主轴转速 | 5510 | 主轴 | 紧急停机 | Rotor Overspeed
312 | 发电机超速 | 5520 | 发电机 | 紧急停机 | (G) Overspeed
319 | WP2035发电机超速 | 5530 | 发电机 | 紧急停机 | WP2035 (G) Over-speed
320 | WP2035主轴超速 | 5540 | 主轴 | 紧急停机 | WP2035 (R) Over-speed
346 | 发电机转速超过运行最大值 | 5550 | 发电机 | 快速停机 | (G)oversp. operation
352 | 发电机转速震荡 | 5560 | 发电机 | 一般故障停机 | (G)Oscillation
414 | 刹车未释放 | 5570 | 机舱 | 一般故障停机 | Brake not released
415 | 刹车盘磨损报警 | 5580 | 机舱 | 一般故障停机 | Brake pads worn
431 | B50等级刹车时间过长 | 5590 | 主控 | 快速停机 | B50 brake time > max
433 | B199等级刹车时间过长 | 5600 | 主控 | 紧急停机 | B199 brake time >max
439 | 刹车阀故障 | 5610 | 液压站 | 一般故障停机 | Brake valve error
441 | 刹车压力故障 | 5620 | 液压站 | 报警 | Brake pressure
500 | 发电机过热故障重复 | 5630 | 发电机 | 一般故障停机 | (G) Heat Error Repeat
530 | 发电机功率过高 | 5640 | 发电机 | 一般故障停机 | (G) Power Too High
531 | 发电机L1绕组温度报警 | 5650 | 发电机 | 报警 | (G) L1 Temp.
532 | 发电机L1绕组温度停机 | 5660 | 发电机 | 一般故障停机 | (G) L1 Temp. Stop
533 | 发电机L2绕组温度报警 | 5670 | 发电机 | 一般故障停机 | (G) L2 Temp.
534 | 发电机L2绕组温度停机 | 5680 | 发电机 | 一般故障停机 | (G) L2 Temp. Stop
535 | 发电机L3绕组温度报警 | 5690 | 发电机 | 一般故障停机 | (G) L3 Temp.
536 | 发电机L3绕组温度停机 | 5700 | 发电机 | 一般故障停机 | (G) L3 Temp. Stop
549 | 发电机加热器反馈故障 | 5710 | 发电机 | 一般故障停机 | (G) Heating FB
554 | 发电机碳刷报警 | 5720 | 发电机 | 一般故障停机 | (G) Brushes worn
601 | 电网电流不对称 | 5730 | 电网 | 紧急停机 | Current asymmetry
639 | 箱变油位低 | 5740 | 箱变 | 一般故障停机 | Trafo oil level
664 | 箱变温度高报警 | 5750 | 箱变 | 一般故障停机 | Trafo temp.warning
670 | 塔基防雷模块故障 | 5760 | 主控 | 报警 | Lightningprot. tower
671 | 机舱防雷模块故障 | 5770 | 主控 | 报警 | Lightningprot.nacel.
700 | 偏航报警 | 5780 | 偏航 | 一般故障停机 | Error by yawing
701 | 偏航报警重复故障 | 5790 | 偏航 | 一般故障停机 | Rep. error by yawing
706 | 偏航逆时针反馈故障 | 5800 | 偏航 | 一般故障停机 | Yaw CCW feedback
707 | 偏航顺时针反馈故障 | 5810 | 偏航 | 一般故障停机 | Yaw CW feedback
708 | 逆时针解缆 | 5820 | 偏航 | 一般故障停机 | Twisted CCW
709 | 顺时针解缆 | 5830 | 偏航 | 一般故障停机 | Twisted CW
715 | 自动解缆 | 5840 | 偏航 | 一般故障停机 | Cable autounwind
730 | 偏航传感器不匹配 | 5850 | 偏航 | 一般故障停机 | Yaw sensor defect
732 | 手动偏航激活 | 5860 | 偏航 | 报警 | Manual yaw active
734 | 机舱位置与风向偏差过大 | 5870 | 偏航 | 一般故障停机 | Nacel.pos<>windvane
742 | 偏航A/B传感器故障 | 5880 | 偏航 | 一般故障停机 | Yaw sensor A/B
755 | 偏航服务模式 | 5890 | 偏航 | 一般故障停机 | Service yaw
760 | 偏航角度误差 | 5900 | 偏航 | 一般故障停机 | Yaw misalignment
763 | 偏航驱动故障 | 5910 | 偏航 | 一般故障停机 | Yaw sens/drive def.
779 | 自动校准解缆 | 5920 | 偏航 | 一般故障停机 | Auto Calibrate Twist
934 | 发电机风扇反馈故障 | 5930 | 发电机 | 一般故障停机 | (G) Fan FB
1012 | 变频器通讯故障 | 5940 | 变频器 | 紧急停机 | Inverter Com. Error
1023 |  | 5950 | 变频器 | 紧急停机 | Inverter CANopen
1040 |  | 5960 | 变频器 | 紧急停机 | CANopen Plc com
1041 |  | 5970 | 变频器 | 紧急停机 | CANopen plc can com
1045 |  | 5980 | 变频器 | 紧急停机 | CANopen plc EMCY
1047 |  | 5990 | 变频器 | 紧急停机 | CANopen inv. rec.
1048 |  | 6000 | 变频器 | 紧急停机 | CANopen inv. Send
1112 | 自检超时 | 6010 | 主控 | 报警 | Selftest timeout
1113 | 变桨角度不同步 | 6020 | 变桨 | 一般故障停机 | Pitch angle diff.
1119 | 变桨角度与给定值不同步 | 6030 | 变桨 | 一般故障停机 | Pitch pos.<>setpoint
1157 | 变桨控制通讯 | 6040 | 变桨 | 紧急停机 | Pitch ctrl.communic.
1181 | 1号变桨电池电压报警 | 6050 | 变桨 | 一般故障停机 | Batt.voltage 1 warn.
1182 | 1号变桨电池电压停机 | 6060 | 变桨 | 紧急停机 | Batt.voltage 1 stop
1183 | 2号变桨电池电压报警 | 6070 | 变桨 | 一般故障停机 | Batt.voltage 2 warn.
1184 | 2号变桨电池电压停机 | 6080 | 变桨 | 紧急停机 | Batt.voltage 2 stop
1185 | 3号变桨电池电压报警 | 6090 | 变桨 | 一般故障停机 | Batt.voltage 3 warn.
1186 | 3号变桨电池电压停机 | 6100 | 变桨 | 紧急停机 | Batt.voltage 3 stop
1187 | 变桨电池测试 | 6110 | 变桨 | 报警 | Battery test
1201 | 液压站油位低 | 6120 | 液压站 | 一般故障停机 | (H) Oil Level Low
1213 | 液压站工作时间过长 | 6130 | 液压站 | 一般故障停机 | (H) Oper.Time > Max.
1223 | 液压站系统压力高 | 6140 | 液压站 | 报警 | (H) sys. press. high
1224 | 液压站系统压力低 | 6150 | 液压站 | 报警 | (H) sys. press. low
1230 | 液压站油温过热 | 6160 | 液压站 | 一般故障停机 | (H) oil very hot
1232 | 齿轮箱过滤去堵塞 | 6170 | 齿轮箱 | 报警 | Oil filter clogged
1274 | 液压站过载 | 6180 | 齿轮箱 | 一般故障停机 | (H)(P) Overload
1301 | 齿轮箱过滤去故障 | 6190 | 齿轮箱 | 报警 | Gear oil filt.defect
1302 | 齿轮箱冷却风扇反馈故障 | 6200 | 齿轮箱 | 一般故障停机 | Feedback Gear Cooler
1305 | 齿轮箱油位低 | 6210 | 齿轮箱 | 一般故障停机 | Gear Oil Low
1309 | 齿轮箱油泵反馈故障 | 6220 | 齿轮箱 | 一般故障停机 | Gear Oil (P) FB
1323 | 齿轮箱轴承1温度报警 | 6230 | 齿轮箱 | 报警 | Gear bearing temp. 1
1324 | 齿轮箱轴承1温度停机 | 6240 | 齿轮箱 | 一般故障停机 | Gear Bear.Temp.1Stop
1325 | 齿轮箱轴承2温度报警 | 6250 | 齿轮箱 | 报警 | Gear bearing temp. 2
1326 | 齿轮箱轴承2温度停机 | 6260 | 齿轮箱 | 一般故障停机 | Gear Bear.Temp.2Stop
1327 | 齿轮箱油温过热 | 6270 | 齿轮箱 | 报警 | Gear Oil Hot
1328 | 齿轮箱油温低 | 6280 | 齿轮箱 | 一般故障停机 | Gear Oil Temp. Low
1338 | 齿轮箱油压故障 | 6290 | 齿轮箱 | 一般故障停机 | Gear oil press.error
1346 | 齿轮箱油温停机 | 6300 | 齿轮箱 | 一般故障停机 | Gear oil temp. Stop
1359 | 主轴轴承1温度过高 | 6310 | 主轴 | 一般故障停机 | M.bear 1 temp Max-Max
1360 | 主轴轴承1温度高 | 6320 | 主轴 | 报警 | M.bear 1 temp Max
1363 | 主轴轴承2温度过高 | 6330 | 主轴 | 一般故障停机 | M.bear 2 temp Max-Max
1364 | 主轴轴承2温度高 | 6340 | 主轴 | 报警 | M.bear 2 temp Max
1383 | 齿轮箱加热器故障 | 6350 | 齿轮箱 | 一般故障停机 | Gear Heating Failure
1409 | 变频器故障 | 6360 | 变频器 | 报警 | Freq.conv. error
1413 | 变频器跳闸 | 6370 | 变频器 | 快速停机 | Freq.cnv. tripped
1511 | WP4084通道1故障 | 6380 | 机舱 | 一般故障停机 | WP4084 chan. 1 def.
1512 | WP4084通道2故障 | 6390 | 机舱 | 一般故障停机 | WP4084 chan. 2 def.
1513 | WP4084通讯故障 | 6400 | 机舱 | 一般故障停机 | WP4084 comm. error
1539 | 1号WP4084通道1超限1 | 6410 | 机舱 | 一般故障停机 | WP4084No1 CH1 level 1
1544 | PT100故障 | 6420 | 主控 | 一般故障停机 | PT100 Defective
1555 | 1号WP4084通道2超限1 | 6430 | 主控 | 一般故障停机 | WP4084No1 CH2 level 1
1556 | 1号WP4084通道1超限2 | 6440 | 主控 | 一般故障停机 | WP4084No1 CH1 level 2
1557 | 2号WP4084通道2超限2 | 6450 | 主控 | 一般故障停机 | WP4084No1 CH2 level 2
1558 | 2号WP4084通道1超限1 | 6460 | 主控 | 一般故障停机 | WP4084No2 CH1 level 1
1559 | 2号WP4084通道2超限1 | 6470 | 主控 | 一般故障停机 | WP4084No2 CH2 level 1
1561 | 航空灯供电故障 | 6480 | 机舱 | 报警 | Flight warn.ligh.out
1564 | 2号WP4084通道1超限2 | 6490 | 主控 | 一般故障停机 | WP4084No2 CH1 level 2
1565 | 2号WP4084通道2超限2 | 6500 | 主控 | 一般故障停机 | WP4084No2 CH2 level 2
1569 | 航空灯故障 | 6510 | 机舱 | 报警 | Flight warn.ligh.def
1585 | 主轴锁定 | 6520 | 主轴 | 一般故障停机 | Rotor Locked
1595 | 自检 | 6530 | 主控 | 报警 | Selftest
1672 | 变频器主断路器断开 | 6540 | 变频器 | 快速停机 | F.conv. MCCB open
1684 | 变频器未并网 | 6550 | 变频器 | 快速停机 | F.conv. trans. grid
1689 | 电网连接超时 | 6560 | 变频器 | 快速停机 | Timeout grid connect
1692 | 塔基温度报警 | 6570 | 主控 | 报警 | Tower base temp.warn
1703 | 外部停机 | 6580 | 主控 | 紧急停机 | External Stop
1715 | 4-20mA信号停机 | 6590 | 主控 | 一般故障停机 | 4-20 mA Signal Stop
1733 | 1号WP4084通道1高频振动报警 | 6600 | 主控 | 报警 | High frq. vib.No1 CH1
1734 | 1号WP4084通道2高频振动报警 | 6610 | 主控 | 报警 | High frq. vib.No1 CH2
1748 | 2号WP4084通道1高频振动报警 | 6620 | 主控 | 报警 | High frq. vib.No2 CH1
1749 | 1号WP4084通道2高频振动报警 | 6630 | 主控 | 报警 | High frq. vib.No2 CH2
1769 | 主控模块手动关机 | 6640 | 主控 | 一般故障停机 | Main ctrl.m.shutdown
1832 | B99等级刹车时间过长 | 6650 | 主控 | 紧急停机 | B99 brake time > max
1835 | 刹车故障 | 6660 | 液压站 | 一般故障停机 | Brake failure
1900 | 1号变桨变频器故障 | 6670 | 变桨 | 紧急停机 | Pitch inv. 1 error
1901 | 2号变桨变频器故障 | 6680 | 变桨 | 紧急停机 | Pitch inv. 2 error
1902 | 3号变桨变频器故障 | 6690 | 变桨 | 紧急停机 | Pitch inv. 3 error
1903 | 变桨电池充电器故障 | 6700 | 变桨 | 一般故障停机 | Battery charger err.
1934 | 变桨润滑油空 | 6710 | 变桨 | 一般故障停机 | Pitch Lubr. Empty
1942 | 轮毂服务模式 | 6720 | 变桨 | 报警 | Service active hub
1975 | 1号变桨为准备好 | 6730 | 变桨 | 紧急停机 | Pitch 1 not ready
1976 | 2号变桨为准备好 | 6740 | 变桨 | 紧急停机 | Pitch 2 not ready
1977 | 3号变桨为准备好 | 6750 | 变桨 | 紧急停机 | Pitch 3 not ready
1995 | 1号变桨变频器报警 | 6760 | 变桨 | 一般故障停机 | Pitch inv. 1 warn.
1996 | 2号变桨变频器报警 | 6770 | 变桨 | 一般故障停机 | Pitch inv. 2 warn.
1997 | 3号变桨变频器报警 | 6780 | 变桨 | 一般故障停机 | Pitch inv. 3 warn.
2035 | 发电机轴承驱动端温度报警 | 6790 | 发电机 | 报警 | (G) Bear.DE Temp
2036 | 发电机轴承驱动端温度停机 | 6800 | 发电机 | 一般故障停机 | (G) Bear.DE Temp.Stop
2037 | 发电机轴承非驱动端温度报警 | 6810 | 发电机 | 报警 | (G) Bear.NDE Temp
2038 | 发电机轴承非驱动端温度停机 | 6820 | 发电机 | 一般故障停机 | (G) Bear.NDE Tmp.Stp
2048 | 发电机L1相绕组温度过低 | 6830 | 发电机 | 报警 | (G) L1 Temp. Min.
2049 | 发电机L2相绕组温度过低 | 6840 | 发电机 | 报警 | (G) L2 Temp. Min.
2050 | 发电机L3相绕组温度过低 | 6850 | 发电机 | 报警 | (G) L3 Temp. Min.
2136 | 塔基紧急停机 | 6860 | 主控 | 紧急停机 | Emer.Stop Tower Base
2225 | UPS通讯丢失 | 6870 | 主控 | 一般故障停机 | UPS Comm. Lost
2267 | 主轴承润滑油空 | 6880 | 主轴 | 一般故障停机 | Main bear.lubr.empty
2269 | 1号WP4086过载警告 | 6890 | 主控 | 报警 | WP4086No1 acc. Alarm
2270 | 1号WP4086过载报警 | 6900 | 主控 | 报警 | WP4086No1 acc. warn.
2273 | 1号WP4086等级1警告 | 6910 | 主控 | 报警 | WP4086No1 lev.1 alarm
2274 | 1号WP4086等级1报警 | 6920 | 主控 | 报警 | WP4086No1 lev.1 warn.
2275 | 1号WP4086等级2警告 | 6930 | 主控 | 报警 | WP4086No1 lev.2 alarm
2276 | 1号WP4086等级2报警 | 6940 | 主控 | 报警 | WP4086No1 lev.2 warn.
2277 | 1号WP4086等级3警告 | 6950 | 主控 | 报警 | WP4086No1 lev.3 alarm
2278 | 1号WP4086等级3报警 | 6960 | 主控 | 报警 | WP4086No1 lev.3 warn.
2279 | WP4086通讯故障 | 6970 | 主控 | 报警 | WP4086 Comm. Error
2290 | 1号WP4086日志已完成 | 6980 | 主控 | 报警 | WP4086No1 log ready.
2291 | 1号WP4086内部故障 | 6990 | 主控 | 报警 | WP4086No1 Intern err.
2310 | 齿轮箱油泵油温高 | 7000 | 齿轮箱 | 报警 | Gear oil therm. hot
2316 | 齿轮箱进口油压低 | 7010 | 齿轮箱 | 报警 | Gear oil2 press. Low
2317 | 齿轮箱油泵油温低 | 7020 | 齿轮箱 | 一般故障停机 | Gear oil therm. Low
2403 | 风速仪故障 | 7030 | 机舱 | 一般故障停机 | Anemometers defect
2411 | 自检电网故障 | 7040 | 电网 | 报警 | Selftest gridfault
2412 | 轴流风扇1过载 | 7050 | 机舱 | 一般故障停机 | Airstream fan 1 Ovl.
2419 | 风向仪偏差过大并且结冰 | 7060 | 机舱 | 一般故障停机 | Vane Diff. and Ice
2424 | 风向仪无数值并且结冰 | 7070 | 机舱 | 一般故障停机 | Ice and No Wind Dir.
2429 | 发电机滑环室温度报警 | 7080 | 发电机 | 报警 | Slip Ring Temp
2430 | 急停继电器跳闸 | 7090 | 安全链 | 紧急停机 | Emer.Stop Relay
2434 | 安全链主回路断开 | 7100 | 安全链 | 紧急停机 | Safety Chain MCCB
2435 | 安全链继电器1断开 | 7110 | 安全链 | 紧急停机 | Safety Chain Relay 1
2436 | 安全链继电器2断开 | 7120 | 安全链 | 紧急停机 | Safety Chain Relay 2
2437 | 连续复位故障 | 7130 | 主控 | 快速停机 | Continous Reset
2440 | 手动安全停机 | 7140 | 主控 | 紧急停机 | Manual Safety Stop
2444 | 塔基温度停机 | 7150 | 主控 | 一般故障停机 | Tower base temp.stop
2451 | 以太网交换机故障 | 7160 | 主控 | 报警 | Eth.net Switch
2452 | 机舱烟雾报警 | 7170 | 主控 | 一般故障停机 | Smoke nacelle
2475 | 加热器熔丝反馈故障 | 7180 | 主控 | 一般故障停机 | Fuse Slipring Heaters
2476 | 应用程序未设置 | 7190 | 主控 | 报警 | App. not configured
2607 | 变桨软件版本错误 | 7200 | 变桨 | 紧急停机 | Pitch sw. ver. err.
2611 | 变桨系统参数被更改 | 7210 | 变桨 | 报警 | Pitch param. changed
2612 | 请求超时 | 7220 | 变桨 | 紧急停机 | Request Timeout
2654 | 紧急变桨 | 7230 | 变桨 | 紧急停机 | Emergency Pitching
2806 | 高频降功率 | 7240 | 主控 | 报警 | FRT Power Reduction
2814 | 低电压穿越激活 | 7250 | 主控 | 报警 | LVRT active
2815 | 低电压穿越结束 | 7260 | 主控 | 一般故障停机 | LVRT ended
2816 | 电网频率过低报警 | 7270 | 主控 | 报警 | FRT freq.<unstable
2817 | 电网频率过高报警 | 7280 | 主控 | 报警 | FRT freq.>unstable
2818 | 电网频率震荡超限 | 7290 | 主控 | 一般故障停机 | FRT freq.stop
2819 | 电网电压过低报警 | 7300 | 主控 | 报警 | FRT voltage<unstable
2820 | 电网电压过高报警 | 7310 | 主控 | 报警 | FRT voltage>unstable
2821 | 电网电压震荡超限 | 7320 | 主控 | 一般故障停机 | FRT voltage stop
2921 | 塔基变频器低电压穿越启动 | 7330 | 变频器 | 报警 | INV LVRT
2934 | 转矩给定值变化过高报警 | 7340 | 主控 | 报警 | Torque control
3007 | 发电机滑环室温度停机 | 7350 | 发电机 | 一般故障停机 | Slip Ring Temp
5000 | 箱变35KV空开跳闸 | 7360 | 箱变 | 报警 | 35 kV switch off
5001 | 箱变690V空开跳闸 | 7370 | 箱变 | 报警 | 690 V switch off
5003 | 齿轮箱进口油压停机 | 7380 | 齿轮箱 | 一般故障停机 | Gear oil2 press.stop
5004 | 齿轮箱油泵温度停机 | 7390 | 齿轮箱 | 一般故障停机 | Gear oil therm. stop
5005 | 变桨轴承进口堵塞 | 7400 | 变桨 | 报警 | Pitch Bear. In Blind
5006 | 偏航轴承润滑油堵塞 | 7410 | 偏航 | 报警 | Yaw Bear.Lubr. Blind
5009 | 发电机风扇出口温度报警 | 7420 | 发电机 | 报警 | (G) Fan Outer temp
5010 | 发电机风扇出口温度停机 | 7430 | 发电机 | 一般故障停机 | (G) Fan Outer temp
8404 | 自检1失败 | 7440 | 主控 | 快速停机 | Selftest no. 1
8405 | 自检2失败 | 7450 | 主控 | 快速停机 | Selftest no. 2
8406 | 自检3失败 | 7460 | 主控 | 快速停机 | Selftest no. 3
8407 | 自检4失败 | 7470 | 主控 | 快速停机 | Selftest no. 4
8408 | 自检5失败 | 7480 | 主控 | 快速停机 | Selftest no. 5
8704 | 烟雾报警 | 7490 | 主控 | 一般故障停机 | Smoke detector
40170 | 模块1.1失败 | 7500 | 主控 | 紧急停机 | 1.1 Failed
40171 | 模块1.1状态故障 | 7510 | 主控 | 一般故障停机 | 1.1 Status Error
40172 | 模块1.1温度故障 | 7520 | 主控 | 一般故障停机 | 1.1 Temperature Error
40173 | 模块1.1运行时间故障 | 7530 | 主控 | 报警 | 1.1 Uptime Error
40174 | 模块1.1虚拟状态 | 7540 | 主控 | 报警 | 1.1 Virtual Module
40180 | 模块1.2失败 | 7550 | 主控 | 紧急停机 | 1.2 Failed
40181 | 模块1.2状态故障 | 7560 | 主控 | 一般故障停机 | 1.2 Status Error
40182 | 模块1.2温度故障 | 7570 | 主控 | 一般故障停机 | 1.2 Temperature Error
40183 | 模块1.2运行时间故障 | 7580 | 主控 | 报警 | 1.2 Uptime Error
40184 | 模块1.2虚拟状态 | 7590 | 主控 | 报警 | 1.2 Virtual Module
40190 | 模块1.3失败 | 7600 | 主控 | 紧急停机 | 1.3 Failed
40191 | 模块1.3状态故障 | 7610 | 主控 | 一般故障停机 | 1.3 Status Error
40192 | 模块1.3温度故障 | 7620 | 主控 | 一般故障停机 | 1.3 Temperature Error
40193 | 模块1.3运行时间故障 | 7630 | 主控 | 报警 | 1.3 Uptime Error
40194 | 模块1.3虚拟状态 | 7640 | 主控 | 报警 | 1.3 Virtual Module
40200 | 模块1.4失败 | 7650 | 主控 | 紧急停机 | 1.4 Failed
40201 | 模块1.4状态故障 | 7660 | 主控 | 一般故障停机 | 1.4 Status Error
40202 | 模块1.4温度故障 | 7670 | 主控 | 一般故障停机 | 1.4 Temperature Error
40203 | 模块1.4运行时间故障 | 7680 | 主控 | 报警 | 1.4 Uptime Error
40204 | 模块1.4虚拟状态 | 7690 | 主控 | 报警 | 1.4 Virtual Module
40330 | 模块2.1失败 | 7700 | 主控 | 紧急停机 | 2.1 Failed
40331 | 模块2.1状态故障 | 7710 | 主控 | 一般故障停机 | 2.1 Status Error
40332 | 模块2.1温度故障 | 7720 | 主控 | 一般故障停机 | 2.1 Temperature Error
40333 | 模块2.1运行时间故障 | 7730 | 主控 | 报警 | 2.1 Uptime Error
40334 | 模块2.1虚拟状态 | 7740 | 主控 | 报警 | 2.1 Virtual Module
40490 | 模块3.1失败 | 7750 | 主控 | 紧急停机 | 3.1 Failed
40491 | 模块3.1状态故障 | 7760 | 主控 | 一般故障停机 | 3.1 Status Error
40492 | 模块3.1温度故障 | 7770 | 主控 | 一般故障停机 | 3.1 Temperature Error
40493 | 模块3.1运行时间故障 | 7780 | 主控 | 报警 | 3.1 Uptime Error
40494 | 模块3.1虚拟状态 | 7790 | 主控 | 报警 | 3.1 Virtual Module
40500 | 模块3.2失败 | 7800 | 主控 | 紧急停机 | 3.2 Failed
40501 | 模块3.2状态故障 | 7810 | 主控 | 一般故障停机 | 3.2 Status Error
40502 | 模块3.2温度故障 | 7820 | 主控 | 一般故障停机 | 3.2 Temperature Error
40503 | 模块3.2运行时间故障 | 7830 | 主控 | 报警 | 3.2 Uptime Error
40504 | 模块3.2虚拟状态 | 7840 | 主控 | 报警 | 3.2 Virtual Module
40510 | 模块3.3失败 | 7850 | 主控 | 紧急停机 | 3.3 Failed
40511 | 模块3.3状态故障 | 7860 | 主控 | 一般故障停机 | 3.3 Status Error
40512 | 模块3.3温度故障 | 7870 | 主控 | 一般故障停机 | 3.3 Temperature Error
40513 | 模块3.3运行时间故障 | 7880 | 主控 | 报警 | 3.3 Uptime Error
40514 | 模块3.3虚拟状态 | 7890 | 主控 | 报警 | 3.3 Virtual Module
64000 | WP4000 超温 | 7900 | 主控 | 一般故障停机 | WP4000 Overtemp
64001 | 主控功率过低 | 7910 | 主控 | 紧急停机 | Main power low
64002 | 备份功率过低 | 7920 | 主控 | 紧急停机 | Backup power low
64003 | 文件系统故障 | 7930 | 主控 | 一般故障停机 | File system error
64010 | 操作系统启动 | 7940 | 主控 | 报警 | OS Startup
64011 | 手动重启 | 7950 | 主控 | 紧急停机 | Manual reboot
64012 | 功率不足关机 | 7960 | 主控 | 紧急停机 | Power fail shutdown
64013 | 软件看门狗关机 | 7970 | 主控 | 紧急停机 | SW Watchdog shutdown
64014 | 处理器看门狗关机 | 7980 | 主控 | 紧急停机 | CPU Watchdog shutdown
64015 | 模块硬件故障 | 7990 | 主控 | 紧急停机 | Power On/HW Reset/HW WD
64016 | 未知原因关机 | 8000 | 主控 | 紧急停机 | Unknown shutdown
64017 | 手动关机 | 8010 | 主控 | 紧急停机 | Manual Shutdown
64018 | 操作系统关机 | 8020 | 主控 | 紧急停机 | OS Shutdown
64019 | 应用程序未载入 | 8030 | 主控 | 紧急停机 | Application not loaded
64020 | Guard_Output_12_SC_Missing | 8040 | 主控 | 报警 | Guard_Output_12_SC_Missing
64021 | Guard_Rl1_Allways_ON | 8050 | 主控 | 报警 | Guard_Rl1_Allways_ON
64022 | Guard_Rl1_Allways_OFF | 8060 | 主控 | 报警 | Guard_Rl1_Allways_OFF
64023 | Guard_Rl2_Allways_ON | 8070 | 主控 | 报警 | Guard_Rl2_Allways_ON
64024 | Guard_Rl2_Allways_OFF | 8080 | 主控 | 报警 | Guard_Rl2_Allways_OFF
64025 | Guard_Input_10_SC_Missing | 8090 | 主控 | 报警 | Guard_Input_10_SC_Missing
64026 | 模块初始化故障 | 8100 | 主控 | 报警 | WPLine Init Failed
64027 | 模块设置故障 | 8110 | 主控 | 报警 | WPLine Conf Failed
64028 | 模块设置更改 | 8120 | 主控 | 报警 | WPLine Conf Modified
64029 | 系统报警 | 8130 | 主控 | 报警 | System Warning
64030 | 系统故障 | 8140 | 主控 | 一般故障停机 | System Error
64031 | 新软件 | 8150 | 主控 | 报警 | New Software
64032 | 请求重启 | 8160 | 主控 | 报警 | Request Restart
64033 | 应用程序请求重启 | 8170 | 主控 | 报警 | Application request reboot
64035 | IO报警 | 8180 | 主控 | 报警 | IO Warning
64036 | 看门狗超时 | 8190 | 主控 | 紧急停机 | Watchdog Timeout
64037 | 不完全关机 | 8200 | 主控 | 一般故障停机 | Incomplete shutdown
64038 | 系统重复故障 | 8210 | 主控 | 一般故障停机 | System repeating error
5002 | PPM停机 | 8220 | 主控 | 一般故障停机 | Stop by PPM
5007 | PPM有功通讯中断 | 8230 | 主控 | 报警 | PPMAPComError
5008 | PPM无功通讯中断 | 8240 | 主控 | 报警 | PPMRPComError
5011 | PPM给定无功过高 | 8250 | 主控 | 报警 | RPowerSpTooHigh